## I
SHEET NO.Ⅰ
PROCESS INSTRUMENT LIST INDEX
| CONTENTS |  | SHEET NO.
| PROCESS INSTRUMENT LIST INDEX |  | Ⅰ
| ABBREVIATION LIST |  | Ⅱ,Ⅲ
| NOTE |  | IV
| PROCESS INSTRUMENT LIST |  | 1~180
|  | 1. PRESSURE TRANSMITTER (PT) | 1~5 | 24. PACKAGE SYSTEM INSTRUMENT LIST |  | 137~181
|  | 2. DIFFERENTIAL PRESSURE TRANSMITTER (DPT) | 6~7 |  | AIR CANNON SYSTEM | 137
|  | 3. DIFFERENTIAL PRESSURE GAUGE (DPG) | 8 |  | AIR PRE-HEATER SYSTEM | 138~140
|  | 4. PRESSURE SWITCH (PS) | 9~10 |  | BOTTOM ASH COOLER SYSTEM | 141~146
|  | 5. PRESSURE GAUGE (PG) | 11~19 |  | COAL FEEDER SYSTEM | 147~151
|  | 6. LEVEL TRANSMITTER (LT) | 20~22 |  | DIESEL OIL AND BURNER SYSTEM | 152~162
|  | 7. LEVEL SWITCH (LS) | 23~26 |  | FLUIDIZING AIR SYSTEM | 163~166
|  | 8. LEVEL GAUGE (LG) | 27~29 |  | HYPO-CHLORINATED DOSING SYSTEM | 167
|  | 9. FLOW TRANSMITTER (FT) | 30~31 |  | INDUCED DRAFT FAN | 168~170
|  | 10. FLOW ELEMENT (FE) | 32~34 |  | PRIMARY AIR FAN | 171~172
|  | 11. FLOW GAUGE (FG) | 35~38 |  | PRIMARY AIR FAN LUBE OIL SYSTEM | 173
|  | 12. TEMPERATURE TRANSMITTER (TT) | 39~52 |  | SECOND AIR FAN | 174~180
|  | 13. TEMPERATURE ELEMENT (TE) | 53~70
|  | 14. TEMPERATURE GAUGE (TG) | 71~77
|  | 15. TEST WELL (TW) | 78~91
|  | 16. ANALYZER TRANSMITTER (AT) | 92~94
|  | 17. CONTROL VALVE (CV) | 95~98
|  | 18. SOLENOID VALVE (SV) | 99~101
|  | 19. ON/OFF VALVE (XV) | 102~103
|  | 20. MOV(MV) | 104~107
|  | 21. POSITION SWITCH (ZS) | 108~125
|  | 22. POSITION TRANSMITTER (ZT) | 126~133
|  | 23. VIBRATION TRANSMITTER (VT) | 134~136
|  | 24. PACKAGE SYSTEM INSTRUMENT LIST | 137~180

## II
SHEET NO. Ⅱ
MISCELLANEOUS ABBREVIATIONS
DESCRIPTION | ABB | DESCRIPTION | ABB | DESCRIPTION | ABB | DESCRIPTION | ABB | DESCRIPTION | ABB
ABSOLUTE | ABS | CONTROL | CONT | EXHAUST | EXH | IGNITION OIL | IO | NORMAL | NRM
AUTOMATIC COMB. | ACC | CONTROLLER | CONTR | EXHAUSTER | EXHTR | IMPULSE | IMP | NORTH | N
AFTER | ATR | COOLER | CLR | EXPANSION | EXP | INBOARD | INBD | NOZZLE | NZL
AIR DUCT | AD | COOLERS | CLRS | EXTRACTION | EXT | INCREASE | INC | NUMBER | NO
ALARM | ALM | COOLING | CLG | EXCHANGER | EXCH | INLET | IN
AMPERE | AMP | CRC. WATER | CW |  |  | INNER | INR
ANALYSIS | ANA | CRC. WATER PUMP | CWP | FEEDER | FDR | INSTRUMENT | INSTR | OIL CIRCUIT BKR | OCB
ATTEMPERATOR | ATTEM | CROSSOVER | CROSOVR | FEEDWATER | FW | INSTRUMENT AIR | IA | OUTLET OR OUTER | OUT
ATOMIZING | ATOM | CURRENT | CUR | FINISH | FIN | INTERMEDIATE | INTERME | OUTBOARD | OUTBD
AUXILIARY | AUX | CYLINDER | CYLDR | FORCED DRAFT | FD |  |  | OVER CURRENT | OC
AVERAGE | AVG |  |  | FREQUENCY | FREQ |  |  | OVER LOAD | OL
|  | DAMPER | DMPR | FRONT | FR | JOURNAL | JNL | OXYGEN | O2
BACK UP | BU | DAY TOTAL | DT | FRONT FACE | FF
BALANCED | BAL | DEAERATOR | DEAER | FROM | FM, FR | LEAD | LD
BANK | BK | DECIMALS | DEC | FULL | FL | LEAVING | LVG | PACKING | PKG
BEARING | BRG | DECREASE | DEC | FURNACE | FURN | LEFT SIDE | LS | PANEL | PNL
BISTABLE | BST | DEMINERALIZE | DEMIN | FUEL OIL | FO | LEVEL | LVL | PARTS PER BILLION | PPB
BLOWER | BLWR | DESUPERHEATER | DSH |  |  | LIGHT | LIT | PERFORMANCE | PERF
BOILER | BLR | DEVIATION | DEV |  |  | LIMIT | LMT | PHASE | PH
BOTTOM | BTM | DIFFERENTIAL | DIFF | GENERATOR | GENTR | LUBRICATION | LUBR | PLANT AIR | PA
BOOSTER | BSTR | DISCHARGE | DISCH | GENERATION | GENTN |  |  | POINT | PT
BREAKER | BKR | DISTANCE | DIST | GLAND | GLD |  |  | POLISHER | POLR
BURNERS | BNRS | DIVISION | DIV | GOVERNOR | GVRNR | MAIN OIL PUMP | MOP | POLISHING | POL
|  | DRAIN | DRN | GOVERNOR END | GOV | MANIFOLD | MNF | POSITION | POS
CALCULATED VALUE | C | DRIVE SHAFT | DS | GROSS | GRS | MANUAL | MNL | POWER CENTER | PC
CALIBRATION | CAL | DIFFERENTIAL PRESSURE | DP | GROUND | GRD | MEGAVARS | MVAR | PREHEATER | PHTR
CENTER | CTR |  |  |  |  | MEGAWATTS | MW | PRESSURE | PRESS
CHAMBER | CHMBR | ECCENTRICITY | ECCNTRY |  |  | METAL | MTL | PRIMARY | PRIM
CIRCULATING | CRC | ECONOMIZER | ECON | HEADER | HDR | MEZZANINE | MEZZ | PULVERIZER | PULV
COLD REHEAT | CRH | EFFICIENCY | EFF | HEAT | HT | MILLIAMPERE | MA | PUMP | PP
COMBUSTION | COMB | ELECTRO HYDRAULIC | EH | HEATER | HTR | MILLIVOLT | MV | PUSHBUTTON | PB
COMMON | CMN | EMERGENCY | EMGY | HIGH | HI | MINUTE | MIN
COMPRESSOR | COMPR | EMERGENCY OIL PUMP | EOP | HOT REHEAT | HRH | MONTH | MON | RATE OF CHANGE | ROC
CONDENSATE | COND | END WALL | EWL | HOUR | HR | MOTOR | MTR | REACTIVE | RACT
CONDENSER | CONDR | ENTERING | ETG | HYDROGEN | H2 | MOTOR CONTROL CENTER | MCC | REAR | RR
CONDUCTIVITY | CONDTT | EXCITOR | EXCTR | HYDRAULIC | HYD |  |  | REAR FACE | RF

## III
SHEET NO. Ⅲ
MISCELLANEOUS ABBREVIATIONS
DESCRIPTION | ABB | DESCRIPTION | ABB
RECIRCULATION | REC | TRANSMITTER | X'MTR
RECLAIM | RECLM | TROUBLE | TRBL
REHEATER | RHTR,RH | TURBINE | TURB, TB
RELAY | RLY | TRANSFER | TRANS
RESERVOIR | RES
REVERSE | REV | UNDER VOLTAGE | UNDRV
RIGHT SIDE | RS | UPPER | UR
RUNBACK | RBK | UPPER END | UE
RETURN | RTN | UTILITY DISPATCH CENTER | UDC
SCREEN | SCR
SEAL OIL | SO
SECONDARY | SEC, 2RY | VACUUM | VAC
SUPERHEATER | SH | VALVE | VLV
SEQUENTIAL | SEQ | VERTICAL | VERT
SHALLOW | SHLW | VIBRATION | VIB
SLEEVE | SLV | VOLTAGE | VOLT
SOOT BLOWER | SB
SOUTH | S
STAGE | STG | WATER | WTR
STANDBY | STBY | WATER PUMP | WPP
STATION | STN | WATER TREATMENT | WT
STATOR | STR | WINDBOX | WBX
STORAGE | STRG | WINDING | WDG
STEAM | STM
STEAM AIR HEATER | SAH
SUCTION | SUCT | YARD | YD
SUPERHEATER | SH
SWITCH | SW
SWITCH YARD | SWYD | ZONE | Z
TANK | TK
TEMPERATURE | TEMP
THROTTLE | THR
THRUST | THRS
TOTAL | TT
TRANSFORMER | X'FMR

## IV
SHEET NO. IV
NOTES :
1. | TAG NO. : TO FOLLOW THE CRITERIA OF NUMBERING SYSTEM FOR INSTRUMENTATION.
2. | FUNCTION : TO DESCRIBE THE FUNCTION OF THE INSTRUMENT.
3. | P&ID DIAG : TO INDICATE P&ID DWG NO.
4. | DESIGN CONDITION : TO INDICATE THE DESIGN TEMPERATURE AND PRESSURE CONDITIONS OF THE INSTRUMENT.
5. | RANGE : TO SPECIFY INSTRUMENT SET RANGE OR MEASURING RANGE.
6. | SIGNAL LEVEL : TO INDICATE THE SENSOR SIGNAL SUCH AS mA, mV, OHM, PULSE, DRY CONTACT, 4~20mA, etc.
7. | CONNECTION TO/FROM : TO INDICATE THE SOURCE OR DESTINATION OF THE INSTRUMENT. e.g. DCS MEANS DISTRIBUTED CONTROL SYSTEM.
8. | TYPE : TO INDICATE THE MEASUREING TYPE OF INSTRUMENT SENSOR.
9. | SUPPLY SCOPE : TO INDICATE SUPPLIER NAME OF PACKAGED VENDOR.

## PT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (Kg/cm2G) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE |  | R
[6 empty] | P(Kg/cm2G) | T( ℃ ) |  |  | FROM | TO |  |  | REMARKS | E
V
1 | PT-MS1002 | PT | MS1002 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER PRESSURE TRANSMITTER | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
2 | PT-MS1006-1 | PT | MS1006-1 | #1 MAIN STEAM PRESSURE TRANSMITTER-1 | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
3 | PT-MS1006-2 | PT | MS1006-2 | #1 MAIN STEAM PRESSURE TRANSMITTER-2 | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
4 | PT-MS1021 | PT | MS1021 | #1 HP TURBINE BYPASS OUTLET PRESSURE TRANSMITTER | PD-011 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
5 | PT-CR1003 | PT | CR1003 | #1 COLD REHEAT STEAM PRESSURE TRANSMITTER | PD-012 | 45 | 395 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
6 | PT-CR1006 | PT | CR1006 | #1 REHEATER HEADER PRESSURE TRANSMITTER | PD-012 | 45 | 395 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
7 | PT-HR1001 | PT | HR1001 | #1 REHEATER OUTLET HEADER PRESSURE TRANSMITTER | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
8 | PT-HR1003-1 | PT | HR1003-1 | #1 REHEAT STEAM PRESSURE TRANSMITTER-1 | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
9 | PT-HR1003-2 | PT | HR1003-2 | #1 REHEAT STEAM PRESSURE TRANSMITTER-2 | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
10 | PT-HR1011 | PT | HR1011 | #1 LP TURBINE BYPASS OUTLET PRESSURE TRANSMITTER | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
11 | PT-TS1013 | PT | TS1013 | #1 EXTRACTION STEAM NO.2 PRESSURE TRANSMITTER | PD-013 | 16 | 440 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
12 | PT-TS1017 | PT | TS1017 | #1 EXTRACTION STEAM NO.3 PRESSURE TRANSMITTER | PD-013 | 6.2 | 380 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
13 | PT-TS1022 | PT | TS1022 | #1 EXTRACTION STEAM NO.4 PRESSURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
14 | PT-TS1026 | PT | TS1026 | #1 EXTRACTION STEAM NO.5 PRESSURE TRANSMITTER | PD-013 | 3.6 | 285 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
15 | PT-AS1004 | PT | AS1004 | #1 AUXILIARY STEAM HEADER PRESSURE TRANSMITTER | PD-014 | 13 | 390 | 0~15 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
16 | PT-AS1005 | PT | AS1005 | #1 AUXILIARY STEAM HEADER PRESSURE TRANSMITTER | PD-014 | 13 | 390 | 0~15 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
17 | PT-SB1052 | PT | SB1052 | #1 SOOTBLOWING HEADER STEAM PRESSURE TRANSMITTER | PD-015 | 30 | 360 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
18 | PT-CD1104 | PT | CD1104 | #1 DEAERATOR PRESSURE TRANSMITTER | PD-016 | 8 | 380 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
19 | PT-CD1110 | PT | CD1110 | #1 CONDENSER PRESSURE TRANSMITTER | PD-016 | 1.055 & Full Vaccum | 100 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
20 | PT-CD1117 | PT | CD1117 | #1 CONDENSATE WATER PRESSURE TRANSMITTER | PD-016 | 24 | 65 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
21 | PT-CD1122 | PT | CD1122 | #1 DEAERATOR INLET CONDESATE PRESSURE TRANSMITTER | PD-016 | 24 | 200 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
22 | PT-FW1011 | PT | FW1011 | #1 BFP COMMON DISCHARGE WATER PRESSURE TRANSMITTER | PD-017 | 230 | 180 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
23 | PT-FW1115-A | PT | FW1115-A | #1 BFP(A) SUCTION PRESSURE TRANSMITTER | PD-017 | 10 | 180 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
24 | PT-FW1115-B | PT | FW1115-B | #1 BFP(B) SUCTION PRESSURE TRANSMITTER | PD-017 | 10 | 180 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
25 | PT-HD1101 | PT | HD1101 | #1 LOW PRESSURE HEATER NO.1 STEAM PRESSURE TRANSMITTER | PD-018 | 3.5 & Full Vacuum | 150 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
26 | PT-BR1001-1 | PT | BR1001-1 | #1 DRUM PRESSURE TRANSMITTER-1 | PD-019 | 155 | 343 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
27 | PT-BR1001-2 | PT | BR1001-2 | #1 DRUM PRESSURE TRANSMITTER-2 | PD-019 | 155 | 343 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
28 | PT-BR1130 | PT | BR1130 | #1 SUPERHEATER PANEL NO.2 INLET STEAM PRESSURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
29 | PT-BR1150 | PT | BR1150 | #1 FINAL SUPERHEATER INLET STEAM PRESSURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
30 | PT-FW1160 | PT | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER PRESSURE TRANSMITTER | PD-019 | 230 | 275 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
31 | PT-SW1110-A1 | PT | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
32 | PT-SW1110-A2 | PT | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
33 | PT-SW1110-B1 | PT | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
34 | PT-SW1110-B2 | PT | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
35 | PT-CW1152 | PT | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
36 | PT-CW1153 | PT | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
37 | PT-DO0005 | PT | DO0005 | DIESEL OIL PUMP COMMON DISCHARGE PRESSURE TRANSMITTER | PD-022,1/5 | 25 | 70 | 0~25 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0
38 | PT-DO1008 | PT | DO1008 | #1 DIESEL OIL RETURN PRESSURE TRANSMITTER | PD-022,1/5 | 25 | 70 | 0~25 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0
39 | PT-PA0107 | PT | PA0107 | PA DRYER A OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
40 | PT-PA0127 | PT | PA0127 | PA DRYER B OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
41 | PT-PA0147 | PT | PA0147 | PA DRYER C OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
42 | PT-PA0705-A | PT | PA0705-A | PLANT AIR TANK A PRESSURE TRANSMITTER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
43 | PT-PA0705-B | PT | PA0705-B | PLANT AIR TANK B PRESSURE TRANSMITTER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
44 | PT-IA0107 | PT | IA0107 | INSTRUMENT AIR DRYER A OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
45 | PT-IA0127 | PT | IA0127 | INSTRUMENT AIR DRYER B OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
46 | PT-IA0147 | PT | IA0147 | INSTRUMENT AIR DRYER C OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
47 | PT-IA0706-A | PT | IA0706-A | INSTRUMENT AIR TANK A PRESSURE TRANSMITTER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
48 | PT-IA0706-B | PT | IA0706-B | INSTRUMENT AIR TANK B PRESSURE TRANSMITTER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
49 | PT-PA1705 | PT | PA1705 | PLANT AIR TO UNIT NO.1 PRESSURE TRANSMITTER | PD-023,3/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
50 | PT-IA1128 | PT | IA1128 | #1 AIR BUFFER TANK OF TURNING GEAR PRESSURE TRANSMITTER | PD-023,4/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
51 | PT-IA1706 | PT | IA1706 | INSTRUMENT AIR UNIT NO.1 PRESSURE TRANSMITTER | PD-023,5/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
52 | PT-IA1064-A | PT | IA1064-A | # 1 AIR BUFFER TANK OF BIASING DAMPER A PRESSURE TRANSMITTER | PD-023,6/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
53 | PT-IA1064-B | PT | IA1064-B | # 1 AIR BUFFER TANK OF BIASING DAMPER B PRESSURE TRANSMITTER | PD-023,6/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
54 | PT-MU0709 | PT | MU0709 | MAKE-UP PUMP COMMON HEADER PRESSURE TRANSMITTER | PD-024 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
55 | PT-IW0715 | PT | IW0715 | INDUSTRIAL WATER PUMP COMMON HEADER PRESSURE TRANSMITTER | PD-025 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0
56 | PT-FG1009-A1 | PT | FG1009-A1 | #1 CYCLONE A SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
57 | PT-FG1009-A2 | PT | FG1009-A2 | #1 CYCLONE A SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
58 | PT-FG1009-B1 | PT | FG1009-B1 | #1 CYCLONE B SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
59 | PT-FG1009-B2 | PT | FG1009-B2 | #1 CYCLONE B SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
60 | PT-FG1085 | PT | FG1085 | #1 FURNACE PRESSURE TRANSMITTER (A) | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
61 | PT-FG1086 | PT | FG1086 | #1 FURNACE PRESSURE TRANSMITTER (B) | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
62 | PT-FG1087-1 | PT | FG1087-1 | #1 FURNACE PRESSURE TRANSMITTER (C) -1 | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
63 | PT-FG1087-2 | PT | FG1087-2 | #1 FURNACE PRESSURE TRANSMITTER (C) -2 | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
64 | PT-FG1121 | PT | FG1121 | #1 AIR PRE-HEATER GAS INLET PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 371 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
65 | PT-FG1134 | PT | FG1134 | #1 AIR PRE-HEATER GAS OUTLET PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
66 | PT-FG1141-A | PT | FG1141-A | #1 INDUCED DRAFT FAN INLET FLUE GAS PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
67 | PT-FG1141-B | PT | FG1141-B | #1 INDUCED DRAFT FAN INLET FLUE GAS PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
68 | PT-FG1151 | PT | FG1151 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
69 | PT-FA1075 | PT | FA1075 | #1 PRIMARY AIR PREHEATER INLET AIR PRESSURE TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
70 | PT-FA1078 | PT | FA1078 | #1 PRIMARY AIR PREHEATER OUTLET AIR PRESSURE TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
71 | PT-FA1085 | PT | FA1085 | #1 SECONDARY AIR PREHEATER INLET AIR PRESSURE TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
72 | PT-FA1088 | PT | FA1088 | #1 SECONDARY AIR PREHEATER OUTLET AIR PRESSURE TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
73 | PT-FA1055-A | PT | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLETT PRESSURE TRANSMITTER | PD-054 | -330~8700 mmH2O | 149 | 0~10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
74 | PT-FA1055-B | PT | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET PRESSURE TRANSMITTER | PD-054 | -330~8700 mmH2O | 149 | 0~10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0

## DPT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (Kg/cm2) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | DPT-CD1001 | DPT | CD1001 | #1 CONDENSATE PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-016 | 3.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0
2 | DPT-CD1002 | DPT | CD1002 | #1 CONDENSATE PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-016 | 3.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0
3 | DPT-FW1115-A | DPT | FW1115-A | #1 BFP(A) SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-017 | - | - | 0~0.6 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | PACKAGE (BFP) |  | 0
4 | DPT-FW1115-B | DPT | FW1115-B | #1 BFP(B) SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-017 | - | - | 0~0.6 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | PACKAGE (BFP) |  | 0
5 | DPT-SW1111 | DPT | SW1111 | #1 BALL SEPARATOR L-1111 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~100mBar | AI 4~20mA | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0
6 | DPT-SW1112 | DPT | SW1112 | #1 BALL SEPARATOR L-1112 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~100mBar | AI 4~20mA | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0
7 | DPT-SW1502 | DPT | SW1502 | #1 DEBRIS FILTER S-1502 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~2000 mmH2O | AI 4~20mA | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0
8 | DPT-SW1504 | DPT | SW1504 | #1 DEBRIS FILTER S-1504 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~2000 mmH2O | AI 4~20mA | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0
9 | DPT-CW1108-A | DPT | CW1108-A | #1 AUXILIARY COOLING WATER PUMP A STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
10 | DPT-CW1108-B | DPT | CW1108-B | #1 AUXILIARY COOLING WATER PUMP B STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
11 | DPT-DO0001 | DPT | DO0001 | DIESEL OIL PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-022,1/5 | 7 | 70 | 0~1.0 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0
12 | DPT-MU0709-A | DPT | MU0709-A | MAKE-UP PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
13 | DPT-MU0709-B | DPT | MU0709-B | MAKE-UP PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
14 | DPT-MU0709-C | DPT | MU0709-C | MAKE-UP PUMP C SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
15 | DPT-IW0715-A | DPT | IW0715-A | INDUSTRIAL WATER PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-025 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
16 | DPT-IW0715-B | DPT | IW0715-B | INDUSTRIAL WATER PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-025 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
17 | DPT-FG1052-5 | DPT | FG1052-5 | #1 AIR PREHEATER DIFFERENTIAL PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~3300 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
18 | DPT-FG1081 | DPT | FG1081 | #1 OVERALL FURNACE DIFFERENTIAL PRESSURE TRANSMITTER (A) | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
19 | DPT-FG1082 | DPT | FG1082 | #1 OVERALL FURNACE DIFFERENTIAL PRESSURE TRANSMITTER (B) | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
20 | DPT-FG1083 | DPT | FG1083 | #1 MIDDLE/UPPER FURNACE DIFFERENTIAL PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 1200 | -1500~1500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
21 | DPT-FG1084 | DPT | FG1084 | #1 FURNACE GRATE DIFFERENTIAL PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
22 | DPT-FG1183 | DPT | FG1183 | #1 MIDDLE/UPPER FURNACE DIFFERENTIAL PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 1200 | -1500~1500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI | NEW ADDED | 0
23 | DPT-FG1184 | DPT | FG1184 | #1 FURNACE GRATE DIFFERENTIAL PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI | NEW ADDED | 0

## DPG
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (Kg/cm2) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | DPG-FW1115-A | DPG | FW1115-A | #1 BFP(A) SUCTION STRAINER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~0.6 | - | - | - | - | PACKAGE (BFP) |  | 0
2 | DPG-FW1115-B | DPG | FW1115-B | #1 BFP(B) SUCTION STRAINER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~0.6 | - | - | - | - | PACKAGE (BFP) |  | 0
3 | DPG-LO1115-A | DPG | LO1115-A | #1 BFP(A) LUBE OIL INLET FILTER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~1.6 | - | - | - | - | PACKAGE (BFP) |  | 0
4 | DPG-LO1115-B | DPG | LO1115-B | #1 BFP(B) LUBE OIL INLET FILTER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~1.6 | - | - | - | - | PACKAGE (BFP) |  | 0

## PS
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | SET POINT (Kg/c㎡G) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | PS-CD1110-1 | PS | CD1110-1 | #1 CONDENSER PRESSURE SWITCH-1 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0
2 | PS-CD1110-2 | PS | CD1110-2 | #1 CONDENSER PRESSURE SWITCH-2 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0
3 | PS-CD1110-3 | PS | CD1110-3 | #1 CONDENSER PRESSURE SWITCH-3 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0
4 | PS-CD1117 | PS | CD1117 | #1 CONDENSATE WATER PRESSURE LOW SWITCH | PD-016 | 24 | 65 | 15.5 | DI | FIELD | DCS | BOURDON | FHI |  | 0
5 | PS-LO1115-A1 | PS | LO1115-A1 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-1 (LOW ALARM/STANDBY PUMP START) | PD-017 | - | - | 1.5 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
6 | PS-LO1115-A2 | PS | LO1115-A2 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-2 (NORMAL/START PERMISIVE FOR BFP) | PD-017 | - | - | 2.0 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
7 | PS-LO1115-A3 | PS | LO1115-A3 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-3 (LOW-LOW/MAIN EQUIPMENT TRIP) | PD-017 | - | - | 1 | DI | FIELD | ARP | - | PACKAGE (BFP) |  | 0
8 | PS-LO1115-B1 | PS | LO1115-B1 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-1 (LOW ALARM/STANDBY PUMP START) | PD-017 | - | - | 1.5 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
9 | PS-LO1115-B2 | PS | LO1115-B2 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-2 (NORMAL/START PERMISIVE FOR BFP) | PD-017 | - | - | 2.0 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
10 | PS-LO1115-B3 | PS | LO1115-B3 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-3 (LOW-LOW/MAIN EQUIPMENT TRIP) | PD-017 | - | - | 1 | DI | FIELD | ARP | - | PACKAGE (BFP) |  | 0
11 | PSL-IA1706-NC | PSL | IA1706-NC | INSTRUMENT AIR UNIT NO.1 PRESSURE NOT LOW SWITCH | PD-023,5/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0
12 | PSL-PA1705 | PSL | PA1705 | PLANT AIR TO UNIT NO.1 PRESSURE LOW SWITCH | PD-023-3/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0
13 | PSL-IA1706 | PSL | IA1706 | INSTRUMENT AIR UNIT NO.1 PRESSURE LOW SWITCH | PD-023-5/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0
14 | PSHH-FG1085 | PSHH | FG1085 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
15 | PSHH-FG1085-NC | PSHH | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
16 | PSHH-FG1086 | PSHH | FG1086 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
17 | PSHH-FG1086-NC | PSHH | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
18 | PSHH-FG1087 | PSHH | FG1087 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
19 | PSHH-FG1087-NC | PSHH | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
20 | PSHHH-FG1085 | PSHHH | FG1085 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
21 | PSHHH-FG1085-NC | PSHHH | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
22 | PSHHH-FG1086 | PSHHH | FG1086 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
23 | PSHHH-FG1086-NC | PSHHH | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
24 | PSHHH-FG1087 | PSHHH | FG1087 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
25 | PSHHH-FG1087-NC | PSHHH | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
26 | PSLL-FG1085 | PSLL | FG1085 | #1 FURNACE PRESSURE SWITCH LOW-LOW (A) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
27 | PSLL-FG1085-NC | PSLL | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (A) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
28 | PSLL-FG1086 | PSLL | FG1086 | #1 FURNACE PRESSURE SWITCH LOW-LOW (B) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
29 | PSLL-FG1086-NC | PSLL | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (B) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
30 | PSLL-FG1087 | PSLL | FG1087 | #1 FURNACE PRESSURE SWITCH LOW-LOW (C) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0
31 | PSLL-FG1087-NC | PSLL | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (C) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0

## PG
ITEM | TAG. NO. | TAG. NO. |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (Kg/c㎡G) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | PG-MS1003 | PG | MS1003 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER PRESSURE GAUGE | PD-011 | 144 | 550 | 0~200 | - | - | - | BOURDON | FHI |  | 0
2 | PG-AS1006 | PG | AS1006 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE (START-UP) | PD-014 | 11 | 280 | 0~15 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
3 | PG-AS1007 | PG | AS1007 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-1 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
4 | PG-AS1008 | PG | AS1008 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-2 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
5 | PG-AS1009 | PG | AS1009 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-3 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
6 | PG-AS1011 | PG | AS1011 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-4 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
7 | PG-AS1012 | PG | AS1012 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-5 | PD-014 | Full Vaccum & 0 | 350 | -1~0 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
8 | PG-AS1013 | PG | AS1013 | #1 STEAM JET AIR EJECTOR CONDENSER PRESSURE GAUGE-1 | PD-014 | Full Vaccum & 0 | 350 | -1~0 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
9 | PG-AS1014 | PG | AS1014 | #1 STEAM JET AIR EJECTOR CONDENSER PRESSURE GAUGE-2 | PD-014 | 0.055Kg/c㎡A | 30.2 | -1~1 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0
10 | PG-SB1051 | PG | SB1051 | #1 SOOTBLOWING HEADER STEAM PRESSURE GAUGE | PD-015 | 30 | 360 | 0~50 | - | - | - | BOURDON | FHI |  | 0
11 | PG-CD1101-1 | PG | CD1101-1 | #1 LOW PRESSURE HEATER NO.1 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0
12 | PG-CD1101-2 | PG | CD1101-2 | #1 LOW PRESSURE HEATER NO.1 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0
13 | PG-CD1102-1 | PG | CD1102-1 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0
14 | PG-CD1102-2 | PG | CD1102-2 | #1 LOW PRESSURE HEATER NO.2 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0
15 | PG-CD1103-1 | PG | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0
16 | PG-CD1103-2 | PG | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 200 | 0~25 | - | - | - | BOURDON | FHI |  | 0
17 | PG-CD1104 | PG | CD1104 | #1 DEAERATOR PRESSURE GAUGE | PD-016 | 8 | 380 | 0~10 | - | - | - | BOURDON | FHI |  | 0
18 | PG-CD1110 | PG | CD1110 | #1 CONDENSER PRESSURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | -1~5 | - | - | - | BOURDON | FHI |  | 0
19 | PG-CD1116-A1 | PG | CD1116-A1 | #1 CONDENSATE PUMP A SUCTION PRESSURE GAUGE | PD-016 | 3.5 | 65 | -1~5 | - | - | - | BOURDON | FHI |  | 0
20 | PG-CD1116-A2 | PG | CD1116-A2 | #1 CONDENSATE PUMP A DISCHARGE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0
21 | PG-CD1116-B1 | PG | CD1116-B1 | #1 CONDENSATE PUMP B SUCTION PRESSURE GAUGE | PD-016 | 3.5 | 65 | -1~5 | - | - | - | BOURDON | FHI |  | 0
22 | PG-CD1116-B2 | PG | CD1116-B2 | #1 CONDENSATE PUMP B DISCHARGE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0
23 | PG-CD1117 | PG | CD1117 | #1 CONDENSATE WATER PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0
24 | PG-FW1105-1 | PG | FW1105-1 | #1 HIGH PRESSURE HEATER NO.1 INLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 180 | 0~250 | - | - | - | BOURDON | FHI |  | 0
25 | PG-FW1105-2 | PG | FW1105-2 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 220 | 0~250 | - | - | - | BOURDON | FHI |  | 0
26 | PG-FW1106-1 | PG | FW1106-1 | #1 HIGH PRESSURE HEATER NO.2 INLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 220 | 0~250 | - | - | - | BOURDON | FHI |  | 0
27 | PG-FW1106-2 | PG | FW1106-2 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 275 | 0~250 | - | - | - | BOURDON | FHI |  | 0
28 | PG-FW1115-A1 | PG | FW1115-A1 | #1 BFP(A) DISCHAEGE PRESSURE GAUGE | PD-017 | - | - | 0~250 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
29 | PG-FW1115-A2 | PG | FW1115-A2 | #1 BFP(A) BLEED OFF PRESSURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
30 | PG-FW1115-A3 | PG | FW1115-A3 | #1 BFP(A) SUCTION PRESSURE GAUGE | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
31 | PG-FW1115-A4 | PG | FW1115-A4 | #1 BFP(A) BALANCE LINE PRESSURE GAUGE | PD-017 | - | - | 0~25 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
32 | PG-FW1115-A5 | PG | FW1115-A5 | #1 BFP(A) PUMP DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
33 | PG-FW1115-A6 | PG | FW1115-A6 | #1 BFP(A) PUMP NON DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
34 | PG-FW1115-B1 | PG | FW1115-B1 | #1 BFP(B) DISCHAEGE PRESSURE GAUGE | PD-017 | - | - | 0~250 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
35 | PG-FW1115-B2 | PG | FW1115-B2 | #1 BFP(B) BLEED OFF PRESSURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
36 | PG-FW1115-B3 | PG | FW1115-B3 | #1 BFP(B) SUCTION PRESSURE GAUGE | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
37 | PG-FW1115-B4 | PG | FW1115-B4 | #1 BFP(B) BALANCE LINE PRESSURE GAUGE | PD-017 | - | - | 0~25 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
38 | PG-FW1115-B5 | PG | FW1115-B5 | #1 BFP(B) PUMP DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
39 | PG-FW1115-B6 | PG | FW1115-B6 | #1 BFP(B) PUMP NON DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
40 | PG-LO1115-A1 | PG | LO1115-A1 | #1 BFP(A) LUBE OIL PRESSURE GAUGE-1 | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
41 | PG-LO1115-A2 | PG | LO1115-A2 | #1 BFP(A) LUBE OIL PRESSURE GAUGE-2 | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
42 | PG-LO1115-B1 | PG | LO1115-B1 | #1 BFP(B) LUBE OIL PRESSURE GAUGE-1 | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
43 | PG-LO1115-B2 | PG | LO1115-B2 | #1 BFP(B) LUBE OIL PRESSURE GAUGE-2 | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0
44 | PG-HD1101 | PG | HD1101 | #1 LOW PRESSURE HEATER NO.1 STEAM PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0
45 | PG-HD1102 | PG | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0
46 | PG-HD1102-1 | PG | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 STEAM PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0
47 | PG-HD1103 | PG | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 200 | 0~5 | - | - | - | BOURDON | FHI |  | 0
48 | PG-HD1103-1 | PG | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 STEAM PRESSURE GAUGE | PD-018 | 3.6 | 210 | 0~5 | - | - | - | BOURDON | FHI |  | 0
49 | PG-HD1105 | PG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN PRESSURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | 0~25 | - | - | - | BOURDON | FHI |  | 0
50 | PG-HD1105-1 | PG | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 STEAM PRESSURE GAUGE | PD-018 | 16 | 440 | 0~25 | - | - | - | BOURDON | FHI |  | 0
51 | PG-HD1106 | PG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN PRESSURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | 0~50 | - | - | - | BOURDON | FHI |  | 0
52 | PG-HD1106-1 | PG | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 STEAM PRESSURE GAUGE | PD-018 | 45 | 395 | 0~50 | - | - | - | BOURDON | FHI |  | 0
53 | PG-BD1050 | PG | BD1050 | #1 FLASH TANK PRESSURE GAUGE | PD-019 | 12.5 | 200 | 0~15 | - | - | - | BOURDON | FHI |  | 0
54 | PG-BR1001 | PG | BR1001 | #1 DRUM PRESSURE GAUGE | PD-019 | 155 | 343 | 0~200 | - | - | - | BOURDON | FHI |  | 0
55 | PG-SW1107-A1 | PG | SW1107-A1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
56 | PG-SW1107-A2 | PG | SW1107-A2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
57 | PG-SW1107-B1 | PG | SW1107-B1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
58 | PG-SW1107-B2 | PG | SW1107-B2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
59 | PG-SW1107-C1 | PG | SW1107-C1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
60 | PG-SW1107-C2 | PG | SW1107-C2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
61 | PG-SW1110-A1 | PG | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
62 | PG-SW1110-A2 | PG | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
63 | PG-SW1110-B1 | PG | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
64 | PG-SW1110-B2 | PG | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
65 | PG-SW1113-1 | PG | SW1113-1 | #1 BALL RECIRCULATING PUMP M-1113 SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~2.5 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0
66 | PG-SW1113-2 | PG | SW1113-2 | #1 BALL RECIRCULATING PUMP M-1113 DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~4 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0
67 | PG-SW1114-1 | PG | SW1114-1 | #1 BALL RECIRCULATING PUMP M-1114 SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~2.5 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0
68 | PG-SW1114-2 | PG | SW1114-2 | #1 BALL RECIRCULATING PUMP M-1114 DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~4 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0
69 | PG-SW1501-A | PG | SW1501-A | #1 SEAWATER PUMP (A) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
70 | PG-SW1501-B | PG | SW1501-B | #1 SEAWATER PUMP (B) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
71 | PG-SW1501-C | PG | SW1501-C | #1 SEAWATER PUMP (C) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
72 | PG-SW1503-A1 | PG | SW1503-A1 | #1 SEAWATER BOOSTER PUMP A SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
73 | PG-SW1503-A2 | PG | SW1503-A2 | #1 SEAWATER BOOSTER PUMP A DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
74 | PG-SW1503-B1 | PG | SW1503-B1 | #1 SEAWATER BOOSTER PUMP B SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
75 | PG-SW1503-B2 | PG | SW1503-B2 | #1 SEAWATER BOOSTER PUMP B DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
76 | PG-SW1503-C1 | PG | SW1503-C1 | #1 SEAWATER BOOSTER PUMP C SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0
77 | PG-SW1503-C2 | PG | SW1503-C2 | #1 SEAWATER BOOSTER PUMP C DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
78 | PG-SW1552 | PG | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0
79 | PG-CW1108-A | PG | CW1108-A | #1 AUXILIARY COOLING WATER PUMP A DISCHARGE PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
80 | PG-CW1108-B | PG | CW1108-B | #1 AUXILIARY COOLING WATER PUMP B DISCHARGE PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
81 | PG-CW1151 | PG | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK OUTLET PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
82 | PG-CW1157-A | PG | CW1157-A | #1 AUXILIARY COOLING WATER PUMP (A) SUCTION PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
83 | PG-CW1157-B | PG | CW1157-B | #1 AUXILIARY COOLING WATER PUMP (B) SUCTION PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
84 | PG-DO0004 | PG | DO0004 | DIESEL OIL PUMP COMMON DISCHARGE PRESSURE GAUGE | PD-022,1/5 | 25 | 70 | 0~25 | - | - | - | BOURDON | FHI |  | 0
85 | PG-DO1007 | PG | DO1007 | #1 DIESEL OIL RETURN PRESSURE GAUGE | PD-022,1/5 | 25 | 70 | 0~25 | - | - | - | BOURDON | FHI |  | 0
86 | PG-PA0705A | PG | PA0705A | #1 PLANT AIR TANK T-0705A PRESSURE GAUGE | PD-023,1/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0
87 | PG-PA0705B | PG | PA0705B | #1 PLANT AIR TANK T-0705B PRESSURE GAUGE | PD-023,1/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0
88 | PG-PA0706A | PG | PA0706A | #1 INSTRUMENT AIR TANK T-0706A PRESSURE GAUGE | PD-023,2/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0
89 | PG-PA0706B | PG | PA0706B | #1 INSTRUMENT AIR TANK T-0706B PRESSURE GAUGE | PD-023,2/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0
90 | PG-IA1128 | PG | IA1128 | #1 AIR BUFFER TANK OF TURNING GEAR PRESSURE GAUGE | PD-023,4/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0
91 | PG-IA1064-A | PG | IA1064-A | #1 AIR BUFFER TANK OF BIASING DAMPER A PRESSURE GAUGE | PD-023,5/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0
92 | PG-IA1064-B | PG | IA1064-B | #1 AIR BUFFER TANK OF BIASING DAMPER B PRESSURE GAUGE | PD-023,5/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0
93 | PG-DW0858-A | PG | DW0858-A | REGENERATION WATER PUMP P-0858A DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0
94 | PG-DW0858-B | PG | DW0858-B | REGENERATION WATER PUMP P-0858B DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0
95 | PG-DW0858-C | PG | DW0858-C | REGENERATION WATER PUMP P-0858C DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0
96 | PG-MU0709-A | PG | MU0709-A | MAKE-UP PUMP A DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0
97 | PG-MU0709-B | PG | MU0709-B | MAKE-UP PUMP B DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0
98 | PG-MU0709-C | PG | MU0709-C | MAKE-UP PUMP C DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0
99 | PG-IW0715-A | PG | IW0715-A | INDUSTRIAL WATER PUMP A DISCHARGE PRESSURE GAUGE | PD-025 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
100 | PG-IW0715-B | PG | IW0715-B | INDUSTRIAL WATER PUMP B DISCHARGE PRESSURE GAUGE | PD-025 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
101 | PG-IW0808-A | PG | IW0808-A | ACTIVATED CARBON FILTER FEED PUMP P-0808A DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
102 | PG-IW0808-B | PG | IW0808-B | ACTIVATED CARBON FILTER FEED PUMP P-0808B DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
103 | PG-IW0809-A | PG | IW0809-A | ACTIVATED CARBON FILTER BACKWASH PUMP P-0809A DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
104 | PG-IW0809-B | PG | IW0809-B | ACTIVATED CARBON FILTER BACKWASH PUMP P-0809B DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
105 | PG-IW0895-A | PG | IW0895-A | UTILITY WATER PUMP P-0895A DISCHARGE PRESSURE GAUGE | PD-025 | 4 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0
106 | PG-IW0895-B | PG | IW0895-B | UTILITY WATER PUMP P-0895B DISCHARGE PRESSURE GAUGE | PD-025 | 4 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0
107 | PG-IW0052 | PG | IW0052 | INDUSTRIAL WATER FOR WASTE WATER PUMP 0050A PRESSURE GAUGE | PD-040 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
108 | PG-IW0053 | PG | IW0053 | INDUSTRIAL WATER FOR WASTE WATER PUMP 0050B PRESSURE GAUGE | PD-040 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0
109 | PG-WW0058-A | PG | WW0058-A | WASTEWATER PUMP P-0058A DISCHARGE PRESSURE GAUGE | PD-040 | 7 | 90 | 0~10 | - | - | - | BOURDON | FHI |  | 0
110 | PG-WW0058-B | PG | WW0058-B | WASTEWATER PUMP P-0058B DISCHARGE PRESSURE GAUGE | PD-040 | 7 | 90 | 0~10 | - | - | - | BOURDON | FHI |  | 0
111 | PG-CH1107A | PG | CH1107A | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE DOSING PUMP Z-1107A DISCHARGE PRESSURE GAUGE | PD-042 | 184.62 | 35 | 0~250 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
112 | PG-CH1107B | PG | CH1107B | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE DOSING PUMP Z-1107B DISCHARGE PRESSURE GAUGE | PD-042 | 184.62 | 35 | 0~250 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
113 | PG-CH1108A | PG | CH1108A | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE DOSING PUMP Z-1108A DISCHARGE PRESSURE GAUGE | PD-042 | 18.36 | 35 | 0~40 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
114 | PG-CH1108B | PG | CH1108B | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE DOSING PUMP Z-1108B DISCHARGE PRESSURE GAUGE | PD-042 | 18.36 | 35 | 0~40 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
115 | PG-CH1109A | PG | CH1109A | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE DOSING PUMP Z-1109A DISCHARGE PRESSURE GAUGE | PD-042 | 12.24 | 35 | 0~20 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
116 | PG-CH1109B | PG | CH1109B | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE DOSING PUMP Z-1109B DISCHARGE PRESSURE GAUGE | PD-042 | 12.24 | 35 | 0~20 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
117 | PG-CW1140-1 | PG | CW1140-1 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY PRESSURE GAUGE UPSTREAM Y-STRAINER | PD-044 | 5 | 40 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
118 | PG-CW1140-2 | PG | CW1140-2 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY PRESSURE GAUGE DOWWNSTREAM Y-STRAINER | PD-044 | 5 | 40 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
119 | PG-CW1140-4 | PG | CW1140-4 | #1 SAMPLING SYSTEM CHILLER UNIT COOLING WATER SUPPLY PRESSURE GAUGE UPSTREAM Y-STRAINER | PD-044 | 0.5 | 30 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
120 | PG-CW1140-5 | PG | CW1140-5 | #1 SAMPLING SYSTEM CHILLER UNIT COOLING WATER SUPPLY PRESSURE GAUGE DOWNSTREAM Y-STRAINER | PD-044 | 0.5 | 30 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
121 | PG-SP1001 | PG | SP1001 | #1 DEAERATOR UPSTREAM PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
122 | PG-SP1002 | PG | SP1002 | #1 DEAERATOR OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
123 | PG-SP1003 | PG | SP1003 | #1 MAKE-UP WATER PUMP OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
124 | PG-SP1004 | PG | SP1004 | #1 ECONOMIZER INLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
125 | PG-SP1005 | PG | SP1005 | #1 DRUM WATER (BLOW DOWN) PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
126 | PG-SP1006 | PG | SP1006 | #1 SATURATED STEAM PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
127 | PG-SP1007 | PG | SP1007 | #1 MAIN STEAM LINE PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
128 | PG-SP1008 | PG | SP1008 | #1 CONDENSATE PUMP OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0
129 | PG-RW0862-A | PG | RW0862-A | RAW WATER FEED PUMP P-0862A DISCHARGE PRESSURE GAUGE | PD-045 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0
130 | PG-RW0862-B | PG | RW0862-B | RAW WATER FEED PUMP P-0862B DISCHARGE PRESSURE GAUGE | PD-045 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0
131 | PG-CD1716A | PG | CD1716A | #1 CONDENSATE BOOSTER PUMP P-1716A DISCHARGE PRESSURE GAUGE | PD-047 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0
132 | PG-CD1716B | PG | CD1716B | #1 CONDENSATE BOOSTER PUMP P-1716B DISCHARGE PRESSURE GAUGE | PD-047 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI | NEW ADDED | 0
133 | PG-FA1055-A | PG | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET PRESSURE GAUGE | PD-054,1/3 | 8700 mmH2O | 150 | 0~10000 mmH2O | - | - | - | DIAPHRAGM | FHI |  | 0
134 | PG-FA1055-B | PG | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET PRESSURE GAUGE | PD-054,1/3 | 8700 mmH2O | 150 | 0~10000 mmH2O | - | - | - | DIAPHRAGM | FHI |  | 0

## LT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (mm) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | LT-CD1104-1 | LT | CD1104-1 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-1 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
2 | LT-CD1104-2 | LT | CD1104-2 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-2 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
3 | LT-CD1104-3 | LT | CD1104-3 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-3 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
4 | LT-CD1110 | LT | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL TRANSMITTER | PD-016 | Full Vaccum & 1.03 | 120 | 0~900 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
5 | LT-HD1101-1 | LT | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 LEVEL TRANSMITTER-1 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
6 | LT-HD1101-2 | LT | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 LEVEL TRANSMITTER-2 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
7 | LT-HD1102-1 | LT | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 LEVEL TRANSMITTER-1 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
8 | LT-HD1102-2 | LT | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 LEVEL TRANSMITTER-2 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
9 | LT-HD1103-1 | LT | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 LEVEL TRANSMITTER-1 | PD-018 | 3.6 | 210 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
10 | LT-HD1103-2 | LT | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 LEVEL TRANSMITTER-2 | PD-018 | 3.6 | 210 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
11 | LT-HD1105-1 | LT | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 LEVEL TRANSMITTER-1 | PD-018 | 16 | 440 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
12 | LT-HD1105-2 | LT | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 LEVEL TRANSMITTER-2 | PD-018 | 16 | 440 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
13 | LT-HD1106-1 | LT | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 LEVEL TRANSMITTER-1 | PD-018 | 45 | 395 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
14 | LT-HD1106-2 | LT | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 LEVEL TRANSMITTER-2 | PD-018 | 45 | 395 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0
15 | LT-BR1001-1 | LT | BR1001-1 | #1 DRUM LEVEL -1 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
16 | LT-BR1001-2 | LT | BR1001-2 | #1 DRUM LEVEL -2 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
17 | LT-BR1001-3 | LT | BR1001-3 | #1 DRUM LEVEL -3 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
18 | LT-SW1501 | LT | SW1501 | #1 SEAWATER PUMP INLET LEVEL TRANSMITTER | PD-020 | 1 | 65 | 0.5~15M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0
19 | LT-CW1109 | LT | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL TRANSMITTER | PD-021 | 10 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
20 | LT-DO0701 | LT | DO0701 | OIL SERVICE TANK LEVEL TRANSMITTER | PD-022,1/5 | 1.5 | 70 | 0~8.2 M | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
21 | LT-MU0708-A | LT | MU0708-A | DEMINERALIZED WATER TANK A LEVEL TRANSMITTER | PD-024 | 1.5 | 65 | 0~15M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
22 | LT-MU0708-B | LT | MU0708-B | DEMINERALIZED WATER TANK B LEVEL TRANSMITTER | PD-024 | 1.5 | 65 | 0~15M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
23 | LT-IW0113 | LT | IW0113 | TURBINE BUILDING PLUMBING WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
24 | LT-IW0714 | LT | IW0714 | INDUSTRIAL WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~8.2 M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
25 | LT-IW0724 | LT | IW0724 | FIRE WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~8.2 M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
26 | LT-PW0114 | LT | PW0114 | TURBINE BUILDING POTABLE WATER TANK LEVEL TRANSMITTER | PD-026 | 3 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
27 | LT-PW0721 | LT | PW0721 | WATER TREATMENT PLANT CONTROL BUILDING POTABLE WATER TANK LEVEL TRANSMITTER | PD-026 | 3 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0
28 | LT-RW0717 | LT | RW0717 | RAW WATER PIT LEVEL TRANSMITTER | PD-045 | 1 | 45 | 0.5~5M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0
29 | LT-CL1008-A | LT | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0
30 | LT-CL1008-B | LT | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0
31 | LT-CL1008-C | LT | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0

## LS
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | SET POINT (mm) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | LS-CR1001-1 | LS | CR1001-1 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 HIGH LEVEL SWITCH | PD-011 | 45 | 395 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
2 | LS-CR1001-2 | LS | CR1001-2 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 HIGH-HIGH LEVEL SWITCH | PD-011 | 45 | 395 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
3 | LSLL-CD1104-4 | LSLL | CD1104-4 | #1 DEAERATOR STORAGE TANK WATER LEVEL LOW-LOW SWITCH-4 | PD-016 | 8 | 170 | - | DI | FIELD | ARP | FLOAT | FHI |  | 0
4 | LSLL-CD1110 | LSLL | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL(LOW-LOW) SWITCH | PD-016 | Full Vaccum & 1.03 | 120 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
5 | LSHH-CD1110 | LSHH | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL(HIGH-HIGH) SWITCH | PD-016 | Full Vaccum & 1.03 | 120 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
6 | LS-FW1115-A | LS | FW1115-A | #1 BFP(A) MOTOR LEAKAGE DETECTOR | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
7 | LS-FW1115-B | LS | FW1115-B | #1 BFP(B) MOTOR LEAKAGE DETECTOR | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
8 | LS-LO1115-A | LS | LO1115-A | #1 BFP(A) LUBE OIL LEVEL SWITCH (LOW ALARM) | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
9 | LS-LO1115-B | LS | LO1115-B | #1 BFP(B) LUBE OIL LEVEL SWITCH (LOW ALARM) | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0
10 | LS-HD1101 | LS | HD1101 | #1 LOW PRESSURE HEATER NO.1 LEVEL SWITCH-3 | PD-018 | Full Vaccum & 3.6 | 150 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
11 | LS-HD1102 | LS | HD1102 | #1 LOW PRESSURE HEATER NO.2 LEVEL SWITCH-3 | PD-018 | Full Vaccum & 3.6 | 150 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
12 | LS-HD1103 | LS | HD1103 | #1 LOW PRESSURE HEATER NO.3 LEVEL SWITCH-3 | PD-018 | 3.6 | 200 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
13 | LS-HD1105 | LS | HD1105 | #1 HIGH PRESSURE HEATER NO.1 LEVEL SWITCH-3 | PD-018 | 16 | 210 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
14 | LS-HD1106 | LS | HD1106 | #1 HIGH PRESSURE HEATER NO.2 LEVEL SWITCH-3 | PD-018 | 45 | 260 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
15 | LSH-BR1001-1 | LSH | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0
16 | LSHH-BR1001-1 | LSHH | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (HIGH HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0
17 | LSL-BR1001-1 | LSL | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0
18 | LSLL-BR1001-1 | LSLL | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0
19 | LSLL-BR1001-1-NC | LSLL | BR1001-1-NC | #1 DRUM LEVEL SWITCH-1 (NOT LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0
20 | LSH-BR1001-2 | LSH | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0
21 | LSHH-BR1001-2 | LSHH | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (HIGH HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0
22 | LSL-BR1001-2 | LSL | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0
23 | LSLL-BR1001-2 | LSLL | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0
24 | LSLL-BR1001-2-NC | LSLL | BR1001-2-NC | #1 DRUM LEVEL SWITCH-2 ( NOT LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0
25 | LSLL-CW1109 | LSLL | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL LOW-LOW SWITCH | PD-021 | 10 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0
26 | LS-MU0708-A | LS | MU0708-A | DEMINERALIZED WATER TANK A LEVEL LOW SWITCH | PD-024 | 1.5 | 65 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
27 | LS-MU0708-B | LS | MU0708-B | DEMINERALIZED WATER TANK B LEVEL LOW SWITCH | PD-024 | 1.5 | 65 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
28 | LS-IW0714 | LS | IW0714 | INDUSTRIAL WATER TANK LEVEL LOW SWITCH | PD-025 | 1.5 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0
29 | LS-IW0724 | LS | IW0724 | FIRE WATER TANK LEVEL LOW SWITCH | PD-025 | 1.5 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0
30 | LS-FS1410 | LS | FS1410 | #1 FLASH PIPE LEVEL HIGH SWITCH | PD-027 | 3 | 410 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
31 | LS-FS1411 | LS | FS1411 | #1 FLASH PIPE LEVEL LOW SWITCH | PD-027 | 3 | 410 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0
32 | LS-WW0058 | LS | WW0058 | WASTEWATER PIT T-0058 LEVEL SWITCH(HIGH-HIGH, HIGH, LOW, LOW-LOW) | PD-040 | 0.3 | 95 | - | DI | FIELD | LCP | ELECTRODE | FHI |  | 0
33 | LS-WW1127 | LS | WW1127 | #1 TRANSFORMER AREA PIT A LEVEL SWITCH (LO-LO/LO/HI/HI-HI) | PD-040 | 0.25 | 45 |  | DI | FIELD | LCP | ELECTRODE | FHI |  | 0
34 | LSLL-CH1101 | LSLL | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
35 | LSL-CH1101 | LSL | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
36 | LSH-CH1101 | LSH | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
37 | LSLL-CH1103 | LSLL | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
38 | LSL-CH1103 | LSL | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
39 | LSH-CH1103 | LSH | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
40 | LSLL-CH1105 | LSLL | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
41 | LSL-CH1105 | LSL | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
42 | LSH-CH1105 | LSH | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0
43 | LSL-CL1008-A | LSL | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0
44 | LSH-CL1008-A | LSH | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0
45 | LSL-CL1008-B | LSL | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0
46 | LSH-CL1008-B | LSH | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0
47 | LSL-CL1008-C | LSL | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0
48 | LSH-CL1008-C | LSH | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0
49 | LSLL-CH0701 | LSLL | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0
50 | LSL-CH0701 | LSL | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL LOW SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0
51 | LSH-CH0701 | LSH | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL HIGH SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0

## LG
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (mm) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | LG-CD1104 | LG | CD1104 | #1 DEAERATOR STORAGE TANK WATER LEVEL GAUGE | PD-016 | 8 | 170 | 0~2550 | - | - | - | MAGNETIC | FHI |  | 0
2 | LG-CD1110 | LG | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL GAUGE | PD-016 | Full Vaccum & 1.03 | 120 | 0~600 | - | - | - | REFLEX | FHI |  | 0
3 | LG-LO1115-A | LG | LO1115-A | #1 BFP(A) LUBE OIL LEVEL GAUGE | PD-017 | - | - | 380 | - | - | - | - | PACKAGE (BFP) |  | 0
4 | LG-LO1115-B | LG | LO1115-B | #1 BFP(B) LUBE OIL LEVEL GAUGE | PD-017 | - | - | 380 | - | - | - | - | PACKAGE (BFP) |  | 0
5 | LG-HD1101 | LG | HD1101 | #1 LOW PRESSURE HEATER NO.1 LEVEL GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | 0~200 | - | - | - | REFLEX | FHI |  | 0
6 | LG-HD1102 | LG | HD1102 | #1 LOW PRESSURE HEATER NO.2 LEVEL GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | 0~200 | - | - | - | REFLEX | FHI |  | 0
7 | LG-HD1103 | LG | HD1103 | #1 LOW PRESSURE HEATER NO.3 LEVEL GAUGE | PD-018 | 3.6 | 200 | 0~200 | - | - | - | REFLEX | FHI |  | 0
8 | LG-HD1105 | LG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 LEVEL GAUGE | PD-018 | 16 | 210 | 0~200 | - | - | - | REFLEX | FHI |  | 0
9 | LG-HD1106 | LG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 LEVEL GAUGE | PD-018 | 45 | 260 | 0~200 | - | - | - | REFLEX | FHI |  | 0
10 | LG-BD1050 | LG | BD1050 | #1 FLASH TANK LEVEL GAUGE | PD-019 | 12.5 | 193 | 0~200 | - | - | - | REFLEX | FHI |  | 0
11 | LG-BR1001-1 | LG | BR1001-1 | #1 DRUM LEVEL GAUGE | PD-019 | 155.4 | 343 | 0~470 | - | - | - | BI-COLOR | FHI |  | 0
12 | LG-BR1001-2 | LG | BR1001-2 | #1 DRUM LEVEL GAUGE | PD-019 | 155.4 | 343 | 0~470 | - | - | - | BI-COLOR | FHI |  | 0
13 | LG-CW1109 | LG | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL GAUGE | PD-021 | 10 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0
14 | LG-DO0701-1 | LG | DO0701-1 | OIL SERVICE TANK LEVEL GAUGE-1 | PD-022,1/5 | 1.5 | 70 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0
15 | LG-DO0701-2 | LG | DO0701-2 | OIL SERVICE TANK LEVEL GAUGE-2 | PD-022,1/5 | 1.5 | 70 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0
16 | LG-DO0701-3 | LG | DO0701-3 | OIL SERVICE TANK LEVEL GAUGE-3 | PD-022,1/5 | 1.5 | 70 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0
17 | LG-DO0701-4 | LG | DO0701-4 | OIL SERVICE TANK LEVEL GAUGE-4 | PD-022,1/5 | 1.5 | 70 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0
18 | LG-DO0701-5 | LG | DO0701-5 | OIL SERVICE TANK LEVEL GAUGE-5 | PD-022,1/5 | 1.5 | 70 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0
19 | LG-MU0708-A | LG | MU0708-A | DEMINERALIZED WATER TANK A LEVEL GAUGE | PD-024 | 1.5 | 65 | 0~15 M | - | - | - | FLOAT | FHI |  | 0
20 | LG-MU0708-B | LG | MU0708-B | DEMINERALIZED WATER TANK B LEVEL GAUGE | PD-024 | 1.5 | 65 | 0~15 M | - | - | - | FLOAT | FHI |  | 0
21 | LG-IW0714-1 | LG | IW0714-1 | INDUSTRIAL WATER TANK LEVEL GAUGE-1 | PD-025 | 1.5 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0
22 | LG-IW0714-2 | LG | IW0714-2 | INDUSTRIAL WATER TANK LEVEL GAUGE-2 | PD-025 | 1.5 | 65 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0
23 | LG-IW0714-3 | LG | IW0714-3 | INDUSTRIAL WATER TANK LEVEL GAUGE-3 | PD-025 | 1.5 | 65 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0
24 | LG-IW0714-4 | LG | IW0714-4 | INDUSTRIAL WATER TANK LEVEL GAUGE-4 | PD-025 | 1.5 | 65 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0
25 | LG-IW0714-5 | LG | IW0714-5 | INDUSTRIAL WATER TANK LEVEL GAUGE-5 | PD-025 | 1.5 | 65 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0
26 | LG-IW0724-1 | LG | IW0724-1 | FIRE WATER TANK LEVEL GAUGE-1 | PD-025 | 1.5 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0
27 | LG-IW0724-2 | LG | IW0724-2 | FIRE WATER TANK LEVEL GAUGE-2 | PD-025 | 1.5 | 65 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0
28 | LG-IW0724-3 | LG | IW0724-3 | FIRE WATER TANK LEVEL GAUGE-3 | PD-025 | 1.5 | 65 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0
29 | LG-IW0724-4 | LG | IW0724-4 | FIRE WATER TANK LEVEL GAUGE-4 | PD-025 | 1.5 | 65 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0
30 | LG-IW0724-5 | LG | IW0724-5 | FIRE WATER TANK LEVEL GAUGE-5 | PD-025 | 1.5 | 65 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0
31 | LG-CH1101 | LG | CH1101 | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE SOLUTION TANK Z-1101 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
32 | LG-CH1102 | LG | CH1102 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1102 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
33 | LG-CH1103 | LG | CH1103 | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE SOLUTION TANK Z-1103 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
34 | LG-CH1104 | LG | CH1104 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1104 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
35 | LG-CH1105 | LG | CH1105 | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE SOLUTION TANK Z-1105 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0
36 | LG-CH1106 | LG | CH1106 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1106 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0

## FT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (T/H) |  | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  | SIGNAL | FROM | TO |  |  |  | E
V
1 | FT-MS1031 | FT | MS1031 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER FLOW TRANSMITTER | PD-011 | 144 | 550 | 0~500 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
2 | FT-CD1115 | FT | CD1115 | #1 LP TURBINE BYPASS SPRAY WATER FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~46 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
3 | FT-CD1120 | FT | CD1120 | #1 CONDENSATE WATER FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
4 | FT-CD1121 | FT | CD1121 | #1 CONDESATE POLISHER SYSTEM INLET FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~200 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
5 | FT-CD1122 | FT | CD1122 | #1 DEAERATOR INLET CONDESATE FLOW TRANSMITTER | PD-016 | 24 | 200 | 0~450 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
6 | FT-FW1007-1 | FT | FW1007-1 | #1 BOILER FEEDWATER FLOW TRANSMITTER-1 | PD-017 | 230 | 275 | 0~550 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
7 | FT-FW1007-2 | FT | FW1007-2 | #1 BOILER FEEDWATER FLOW TRANSMITTER-2 | PD-017 | 230 | 275 | 0~550 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
8 | FT-FW1059 | FT | FW1059 | #1 TURBINE BYPASS DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 100 | 180 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
9 | FT-FW1109 | FT | FW1109 | #1 SUPERHEATER PANEL #1 DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 230 | 275 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
10 | FT-FW1119 | FT | FW1119 | #1 SUPERHEATER PANEL #2 DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 230 | 275 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
11 | FT-FW1149 | FT | FW1149 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 100 | 180 | 0~25 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
12 | FT-HD1102 | FT | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN FLOW TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 150 | 0~27.5 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
13 | FT-HD1103 | FT | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN FLOW TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 200 | 0~15 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
14 | FT-HD1105 | FT | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN FLOW TRANSMITTER | PD-018 | 16 & Full Vaccum | 210 | 0~69 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
15 | FT-HD1106 | FT | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN FLOW TRANSMITTER | PD-018 | 45 & Full Vaccum | 260 | 0~45 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
16 | FT-FA1043-A | FT | FA1043-A | #1 START-UP BURNER(A) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,2/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
17 | FT-FA1043-B | FT | FA1043-B | #1 START-UP BURNER(B) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,3/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
18 | FT-FA1043-C | FT | FA1043-C | #1 START-UP BURNER(C) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,4/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
19 | FT-FA1043-D | FT | FA1043-D | #1 START-UP BURNER(D) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,5/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
20 | FT-FG1057-7 | FT | FG1057-7 | #1 STACK FLUE GAS FLOW TRANSMITTER | PD-051 | 33 mmH2O | 200 | 0~886.6 | WET AI 4~20mA | FIELD | DCS | ULTRASONIC | PACKAGE (CEMS) |  | 0
21 | FT-FA1071 | FT | FA1071 | #1 PRIMARY AIR FAN INLET AIR FLOW TRANSMITTER | PD-052 | 0 | 66 | 0~648 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
22 | FT-FA1079 | FT | FA1079 | #1 PRIMARY AIR SYSTEM FLOW TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~510 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
23 | FT-FA1081 | FT | FA1081 | #1 SECONDARY AIR FAN INLET AIR FLOW TRANSMITTER | PD-053 | 0 | 66 | 0~432 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0
24 | FT-FA1055 | FT | FA1055 | #1 FLUIDIZING AIR BLOWER OUTLET COMMON FLOW TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 150 | 0~35 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0

## FE
| TAG. NO. | TAG. NO. |  |  | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (T/H) | ΔP (mmH2O) | CONNECTION |  |  | SUPPLY SCOPE |  | R
ITEM |  |  |  | FUNCTION |  | P(Kg/c㎡G) | T( ℃ ) | RANGE |  | FROM | TO | TYPE |  | REMARKS | E
V
1 | FE-MS1031 | FE | MS1031 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER FLOW ELEMENT | PD-011 | 144 | 550 | 0~500 | <5000 | - |  | FLOW NOZZLE | FHI |  | 0
2 | FE-CD1115 | FE | CD1115 | #1 LP TURBINE BYPASS SPRAY WATER FLOW ELEMENT | PD-016 | 24 | 65 | 0~46 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0
3 | FE-CD1120 | FE | CD1120 | #1 CONDENSATE WATER FLOW ELEMENT | PD-016 | 24 | 65 | 0~400 | <5000 | - | - | ORIFICE PLATE | FHI |  | 0
4 | FE-CD1121 | FE | CD1121 | #1 CONDESATE POLISHER SYSTEM INLET FLOW ELEMENT | PD-016 | 24 | 65 | 0~200 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0
5 | FE-CD1122 | FE | CD1122 | #1 DEAERATOR IN CONDESATE FLOW ELEMENT | PD-016 | 24 | 200 | 0~450 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0
6 | FE-FW1007 | FE | FW1007 | #1 BOILER FEEDWATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~550 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0
7 | FE-FW1059 | FE | FW1059 | #1 TURBINE BYPASS DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 100 | 180 | 0~40 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0
8 | FE-FW1109 | FE | FW1109 | #1 SUPERHEATER PANEL #1 DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~40 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0
9 | FE-FW1119 | FE | FW1119 | #1 SUPERHEATER PANEL #2 DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~40 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0
10 | FE-FW1149 | FE | FW1149 | #1 REHEATER INLET DESUPEREHEATEREATING SPRAY WATER FLOW ELEMENT | PD-017 | 100 | 180 | 0~25 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0
11 | FE-HD1102 | FE | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN FLOW ELEMENT | PD-018 | 3.6 & Full Vacuum | 150 | 0~27.5 | <125 | - | - | ORIFICE PLATE | FHI |  | 0
12 | FE-HD1103 | FE | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN FLOW ELEMENT | PD-018 | 3.6 & Full Vacuum | 200 | 0~15 | <1200 | - | - | ORIFICE PLATE | FHI |  | 0
13 | FE-HD1105 | FE | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN FLOW ELEMENT | PD-018 | 17 & Full Vacuum | 210 | 0~69 | <1250 | - | - | ORIFICE PLATE | FHI |  | 0
14 | FE-HD1106 | FE | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN FLOW ELEMENT | PD-018 | 47 & Full Vacuum | 260 | 0~45 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0
15 | FE-FA1043-A | FE | FA1043-A | #1 START-UP BURNER(A) HOT SECONDARY AIR FLOW ELEMENT | PD-022,2/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0
16 | FE-FA1043-B | FE | FA1043-B | #1 START-UP BURNER(B) HOT SECONDARY AIR FLOW ELEMENT | PD-022,3/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0
17 | FE-FA1043-C | FE | FA1043-C | #1 START-UP BURNER(C) HOT SECONDARY AIR FLOW ELEMENT | PD-022,4/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0
18 | FE-FA1043-D | FE | FA1043-D | #1 START-UP BURNER(D) HOT SECONDARY AIR FLOW ELEMENT | PD-022,5/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0
19 | FE-FA1071 | FE | FA1071 | #1 PRIMARY AIR FAN INLET AIR FLOW ELEMENT | PD-052 | 0 | 66 | - | - | - | - | VENTURI | PACKAGE (PAF) |  | 0
20 | FE-FA1079 | FE | FA1079 | #1 PRIMARY AIR SYSTEM FLOW ELEMENT | PD-052 | -340~2500 mmH2O | 343 | 0~510 | - | - | - | PITOT TUBE | FHI |  | 0
21 | FE-FA1081 | FE | FA1081 | #1 SECONDARY AIR FAN INLET AIR FLOW ELEMENT | PD-053 | 0 | 66 | - | - | - | - | VENTURI | PACKAGE (SAF) |  | 0
22 | FE-FA1055 | FE | FA1055 | #1 FLUIDIZING AIR BLOWER OUTLET COMMON FLOW ELEMENT | PD-054,1/3 | -340~2500 mmH2O | 150 | 0~35 | - | - | - | PITOT TUBE | FHI |  | 0
23 | FE-FA1009-A1 | FE | FA1009-A1 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT A | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0
24 | FE-FA1009-A2 | FE | FA1009-A2 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT B | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0
25 | FE-FA1009-B1 | FE | FA1009-B1 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT A | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0
26 | FE-FA1009-B2 | FE | FA1009-B2 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT B | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0
27 | FE-FA1061-A1 | FE | FA1061-A1 | #1 COAL FEEDER (A) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0
28 | FE-FA1061-A2 | FE | FA1061-A2 | #1 COAL FEEDER (A) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0
29 | FE-FA1061-A3 | FE | FA1061-A3 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0
30 | FE-FA1061-A4 | FE | FA1061-A4 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0
31 | FE-FA1061-B1 | FE | FA1061-B1 | #1 COAL FEEDER (B) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0
32 | FE-FA1061-B2 | FE | FA1061-B2 | #1 COAL FEEDER (B) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0
33 | FE-FA1061-B3 | FE | FA1061-B3 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0
34 | FE-FA1061-B4 | FE | FA1061-B4 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0
35 | FE-FA1061-C1 | FE | FA1061-C1 | #1 COAL FEEDER (C) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0
36 | FE-FA1061-C2 | FE | FA1061-C2 | #1 COAL FEEDER (C) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0
37 | FE-FA1061-C3 | FE | FA1061-C3 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0
38 | FE-FA1061-C4 | FE | FA1061-C4 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0

## FG
| TAG. NO. |  |  |  | P&ID DWG NO. | DESIGN CONDITION |  | RANGE (T/H) |  | CONNECTION |  |  | SUPPLY SCOPE |  | R
ITEM |  |  |  | FUNCTION |  | P(Kg/c㎡G) | T( ℃ ) | RANGE | SIGNAL | FROM | TO | TYPE |  | REMARKS | E
V
1 | FG-CW1140-6 | FG | CW1140-6 | #1 SAMPLING SYSTEM CHILLER UNIT WATER FLOWMETER | PD-044 | - | - | 1~10L/H | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
2 | FG-CW1140-7 | FG | CW1140-7 | #1 SAMPLING SYSTEM COOLING WATER RETURN LINE FLOWMETER | PD-044 | 5 | 40 | 2.5~25L/H | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
3 | FG-SP1001 | FG | SP1001 | #1 DEAERATOR UPSTREAM FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
4 | FG-SP1002 | FG | SP1002 | #1 DEAERATOR UPSTREAM FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
5 | FG-SP1003 | FG | SP1003 | #1 DEAERATOR OUTLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
6 | FG-SP1004 | FG | SP1004 | #1 DEAERATOR OUTLET FLOWMETER FOR DISSOLVED OXYGEN SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
7 | FG-SP1005 | FG | SP1005 | #1 DEAERATOR OUTLET FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
8 | FG-SP1006 | FG | SP1006 | #1 MAKE-UP WATER PUMP OUTLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
9 | FG-SP1007 | FG | SP1007 | #1 MAKE-UP WATER PUMP OUTLET FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
10 | FG-SP1008 | FG | SP1008 | #1 MAKE-UP WATER PUMP OUTLET FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
11 | FG-SP1009 | FG | SP1009 | #1 ECONOMIZER INLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
12 | FG-SP1010 | FG | SP1010 | #1 ECONOMIZER INLET FLOWMETER FOR DISSOLVED OXYGEN SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
13 | FG-SP1011 | FG | SP1011 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
14 | FG-SP1012 | FG | SP1012 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
15 | FG-SP1013 | FG | SP1013 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
16 | FG-SP1014 | FG | SP1014 | #1 SATURATED STEAM FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
17 | FG-SP1015 | FG | SP1015 | #1 SATURATED STEAM FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
18 | FG-SP1016 | FG | SP1016 | #1 MAIN STEAM LINE FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
19 | FG-SP1017 | FG | SP1017 | #1 MAIN STEAM LINE FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
20 | FG-SP1018 | FG | SP1018 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR 1st CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
21 | FG-SP1019 | FG | SP1019 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR 2nd CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
22 | FG-SP1020 | FG | SP1020 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR SODIUM ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
23 | FG-SP1021 | FG | SP1021 | #1 MAIN STEAM LINE FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0
24 | FG-1401 | FG | 1401 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
25 | FG-1402 | FG | 1402 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
26 | FG-1404 | FG | 1404 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
27 | FG-1405 | FG | 1405 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
28 | FG-1406 | FG | 1406 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
29 | FG-1407 | FG | 1407 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
30 | FG-1408 | FG | 1408 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
31 | FG-1409 | FG | 1409 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
32 | FG-1420 | FG | 1420 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
33 | FG-1422 | FG | 1422 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0
34 | FG-FA1009-A1 | FG | FA1009-A1 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE A | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0
35 | FG-FA1009-A2 | FG | FA1009-A2 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE B | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0
36 | FG-FA1009-B1 | FG | FA1009-B1 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE A | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0
37 | FG-FA1009-B2 | FG | FA1009-B2 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE B | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0
38 | FG-FA1061-A1 | FG | FA1061-A1 | #1 COAL FEEDER (A) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0
39 | FG-FA1061-A2 | FG | FA1061-A2 | #1 COAL FEEDER (A) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0
40 | FG-FA1061-A3 | FG | FA1061-A3 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0
41 | FG-FA1061-A4 | FG | FA1061-A4 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0
42 | FG-FA1061-B1 | FG | FA1061-B1 | #1 COAL FEEDER (B) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0
43 | FG-FA1061-B2 | FG | FA1061-B2 | #1 COAL FEEDER (B) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0
44 | FG-FA1061-B3 | FG | FA1061-B3 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0
45 | FG-FA1061-B4 | FG | FA1061-B4 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0
46 | FG-FA1061-C1 | FG | FA1061-C1 | #1 COAL FEEDER (C) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0
47 | FG-FA1061-C2 | FG | FA1061-C2 | #1 COAL FEEDER (C) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0
48 | FG-FA1061-C3 | FG | FA1061-C3 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0
49 | FG-FA1061-C4 | FG | FA1061-C4 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0

## TT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE ( ℃ ) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | TT-MS1004-1 | TT | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE TRANSMITTER-1 | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
2 | TT-MS1004-2 | TT | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE TRANSMITTER-2 | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
3 | TT-MS1007 | TT | MS1007 | #1 MAIN STEAM TEMPERATURE TRANSMITTER | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
4 | TT-MS1022-1 | TT | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-1 | PD-011 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
5 | TT-MS1022-2 | TT | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-2 | PD-011 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
6 | TT-CR1004 | TT | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE TRANSMITTER | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
7 | TT-CR1005-1 | TT | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
8 | TT-CR1005-2 | TT | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
9 | TT-HR1002-1 | TT | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
10 | TT-HR1002-2 | TT | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
11 | TT-HR1004 | TT | HR1004 | #1 REHEAT STEAM TEMPERATURE TRANSMITTER | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
12 | TT-HR1012-1 | TT | HR1012-1 | #1 LOW PRESSURE TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 15 | 280 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
13 | TT-HR1012-2 | TT | HR1012-2 | #1 LOW PRESSURE TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 15 | 280 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
14 | TT-TS1011 | TT | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE TRANSMITTER | PD-013 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
15 | TT-TS1014 | TT | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE TRANSMITTER | PD-013 | 16 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
16 | TT-TS1018 | TT | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE TRANSMITTER | PD-013 | 6.2 | 380 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
17 | TT-TS1023 | TT | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
18 | TT-TS1027 | TT | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
19 | TT-AS1001 | TT | AS1001 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE TRANSMITTER | PD-014 | 13 | 390 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
20 | TT-AS1003 | TT | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE TRANSMITTER | PD-014 | 13 | 390 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
21 | TT-AS1015 | TT | AS1015 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER | PD-014 | 13 | 300 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
22 | TT-SB1056 | TT | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE TRANSMITTER | PD-015 | 30 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
23 | TT-SB1057 | TT | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE TRANSMITTER | PD-015 | 30 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
24 | TT-CD1101 | TT | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
25 | TT-CD1102 | TT | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
26 | TT-CD1103-1 | TT | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
27 | TT-CD1103-2 | TT | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
28 | TT-CD1104 | TT | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE TRANSMITTER | PD-016 | 8 | 170 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
29 | TT-CD1110-1 | TT | CD1110-1 | #1 CONDENSER HOT WELL WATER TEMPERATURE TRANSMITTER-1 | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
30 | TT-CD1110-2 | TT | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE TRANSMITTER-2 | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
31 | TT-CD1110-3 | TT | CD1110-3 | #1 CONDENSER NECK TEMPERATURE TRANSMITTER | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
32 | TT-CD1110-4 | TT | CD1110-4 | #1 CONDENSER FLASH CHAMBERTEMPERATURE TRANSMITTER | PD-016 | 1.03 & Full Vacuum | 120 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
33 | TT-CD1116-A1 | TT | CD1116-A1 | #1 CONDENSAT PUMP (A) COUPLING TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
34 | TT-CD1116-A3 | TT | CD1116-A3 | #1 CONDENSAT PUMP (A) MOTOR BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
35 | TT-CD1116-A4 | TT | CD1116-A4 | #1 CONDENSAT PUMP (A) MOTOR BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
36 | TT-CD1116-AU | TT | CD1116-AU | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
37 | TT-CD1116-AV | TT | CD1116-AV | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
38 | TT-CD1116-AW | TT | CD1116-AW | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
39 | TT-CD1116-B1 | TT | CD1116-B1 | #1 CONDENSAT PUMP (B) COUPLING TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
40 | TT-CD1116-B3 | TT | CD1116-B3 | #1 CONDENSAT PUMP (B) MOTOR BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
41 | TT-CD1116-B4 | TT | CD1116-B4 | #1 CONDENSAT PUMP (B) MOTOR BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
42 | TT-CD1116-BU | TT | CD1116-BU | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
43 | TT-CD1116-BV | TT | CD1116-BV | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
44 | TT-CD1116-BW | TT | CD1116-BW | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
45 | TT-CD1118 | TT | CD1118 | #1 CONDENSATE WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
46 | TT-CD1119 | TT | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
47 | TT-CD1120 | TT | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
48 | TT-CD1122 | TT | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
49 | TT-FW1010 | TT | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 10 | 180 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
50 | TT-FW1011 | TT | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 180 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
51 | TT-FW1105 | TT | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 220 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
52 | TT-FW1106 | TT | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 275 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
53 | TT-FW1115-A1 | TT | FW1115-A1 | #1 BFP(A) PUMP SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
54 | TT-FW1115-A2 | TT | FW1115-A2 | #1 BFP(A) PUMP SIDE BEARING FRONT(DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
55 | TT-FW1115-A3 | TT | FW1115-A3 | #1 BFP(A) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
56 | TT-FW1115-A4 | TT | FW1115-A4 | #1 BFP(A) MOTOR SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
57 | TT-FW1115-AU | TT | FW1115-AU | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
58 | TT-FW1115-AV | TT | FW1115-AV | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
59 | TT-FW1115-AW | TT | FW1115-AW | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
60 | TT-FW1115-B1 | TT | FW1115-B1 | #1 BFP(B) PUMP SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
61 | TT-FW1115-B2 | TT | FW1115-B2 | #1 BFP(B) PUMP SIDE BEARING FRONT(DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
62 | TT-FW1115-B3 | TT | FW1115-B3 | #1 BFP(B) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
63 | TT-FW1115-B4 | TT | FW1115-B4 | #1 BFP(B) MOTOR SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
64 | TT-FW1115-BU | TT | FW1115-BU | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
65 | TT-FW1115-BV | TT | FW1115-BV | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
66 | TT-FW1115-BW | TT | FW1115-BW | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
67 | TT-HD1102 | TT | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
68 | TT-HD1103 | TT | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
69 | TT-HD1105 | TT | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 16 & Full Vaccum | 210 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
70 | TT-HD1106 | TT | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 45 & Full Vaccum | 260 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
71 | TT-BR1020 | TT | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
72 | TT-BR1030 | TT | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
73 | TT-BR1040 | TT | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
74 | TT-BR1110 | TT | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
75 | TT-BR1120-1 | TT | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE TRANSMITTER-1 | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
76 | TT-BR1120-2 | TT | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE TRANSMITTER-2 | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
77 | TT-BR1130-1 | TT | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
78 | TT-BR1130-2 | TT | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
79 | TT-BR1140-1 | TT | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
80 | TT-BR1140-2 | TT | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
81 | TT-BR1150-1 | TT | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
82 | TT-BR1150-2 | TT | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
83 | TT-FW1160 | TT | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 230 | 275 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
84 | TT-SW1110-A1 | TT | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
85 | TT-SW1110-A2 | TT | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
86 | TT-SW1110-B1 | TT | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
87 | TT-SW1110-B2 | TT | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
88 | TT-SW1501-A3 | TT | SW1501-A3 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
89 | TT-SW1501-A4 | TT | SW1501-A4 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
90 | TT-SW1501-AU | TT | SW1501-AU | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
91 | TT-SW1501-AV | TT | SW1501-AV | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
92 | TT-SW1501-AW | TT | SW1501-AW | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
93 | TT-SW1501-B3 | TT | SW1501-B3 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
94 | TT-SW1501-B4 | TT | SW1501-B4 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
95 | TT-SW1501-BU | TT | SW1501-BU | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
96 | TT-SW1501-BV | TT | SW1501-BV | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
97 | TT-SW1501-BW | TT | SW1501-BW | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
98 | TT-SW1501-C3 | TT | SW1501-C3 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
99 | TT-SW1501-C4 | TT | SW1501-C4 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
100 | TT-SW1501-CU | TT | SW1501-CU | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
101 | TT-SW1501-CV | TT | SW1501-CV | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
102 | TT-SW1501-CW | TT | SW1501-CW | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
103 | TT-CW1108-A3 | TT | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
104 | TT-CW1108-A4 | TT | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR REAR BEARING TEMPERATURE TRANSMITTER-2 | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
105 | TT-CW1108-AU | TT | CW1108-AU | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
106 | TT-CW1108-AV | TT | CW1108-AV | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
107 | TT-CW1108-AW | TT | CW1108-AW | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
108 | TT-CW1108-B3 | TT | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
109 | TT-CW1108-B4 | TT | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
110 | TT-CW1108-BU | TT | CW1108-BU | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
111 | TT-CW1108-BV | TT | CW1108-BV | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
112 | TT-CW1108-BW | TT | CW1108-BW | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
113 | TT-CW1152 | TT | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE TRANSMITTER | PD-021 | 10 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
114 | TT-CW1153 | TT | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE TRANSMITTER | PD-021 | 10 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
115 | TT-FG1009-A | TT | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE TEMPERATURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
116 | TT-FG1009-B | TT | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE TEMPERATURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
117 | TT-FG1056-1 | TT | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
118 | TT-FG1056-2 | TT | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
119 | TT-FG1056-3 | TT | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
120 | TT-FG1056-4 | TT | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
121 | TT-FG1056-U | TT | FG1056-U | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
122 | TT-FG1056-V | TT | FG1056-V | #1 INDUCED DRAFT FAN MOTOR WINDIING (V) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
123 | TT-FG1056-W | TT | FG1056-W | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
124 | TT-FG1057-8 | TT | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | 33 mmH2O | 200 | 0~300 | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0
125 | TT-FG1090-A | TT | FG1090-A | #1 FURNACE FRONT TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
126 | TT-FG1090-B | TT | FG1090-B | #1 FURNACE FRONT TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
127 | TT-FG1090-C | TT | FG1090-C | #1 FURNACE FRONT TEMPERATURE (C) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
128 | TT-FG1090-D | TT | FG1090-D | #1 FURNACE FRONT TEMPERATURE (D) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
129 | TT-FG1090-E | TT | FG1090-E | #1 FURNACE FRONT TEMPERATURE (E) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
130 | TT-FG1090-F | TT | FG1090-F | #1 FURNACE FRONT TEMPERATURE (F) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
131 | TT-FG1090-G | TT | FG1090-G | #1 FURNACE REAR TEMPERATURE (G) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
132 | TT-FG1090-H | TT | FG1090-H | #1 FURNACE REAR TEMPERATURE (H) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
133 | TT-FG1090-I | TT | FG1090-I | #1 FURNACE REAR TEMPERATURE (I) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
134 | TT-FG1091-A | TT | FG1091-A | #1 FURNACE FRONT TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
135 | TT-FG1091-B | TT | FG1091-B | #1 FURNACE FRONT TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
136 | TT-FG1091-C | TT | FG1091-C | #1 FURNACE FRONT TEMPERATURE (C) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
137 | TT-FG1091-D | TT | FG1091-D | #1 FURNACE FRONT TEMPERATURE (D) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
138 | TT-FG1091-E | TT | FG1091-E | #1 FURNACE FRONT TEMPERATURE (E) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
139 | TT-FG1091-F | TT | FG1091-F | #1 FURNACE FRONT TEMPERATURE (F) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
140 | TT-FG1091-G | TT | FG1091-G | #1 FURNACE REAR TEMPERATURE (G) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
141 | TT-FG1091-H | TT | FG1091-H | #1 FURNACE REAR TEMPERATURE (H) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
142 | TT-FG1091-I | TT | FG1091-I | #1 FURNACE REAR TEMPERATURE (I) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
143 | TT-FG1092-A | TT | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
144 | TT-FG1092-B | TT | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
145 | TT-FG1095-A | TT | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE-1 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
146 | TT-FG1095-B | TT | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE-1 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
147 | TT-FG1096-A | TT | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE-2 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
148 | TT-FG1096-B | TT | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE-2 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
149 | TT-FG1100 | TT | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 900 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
150 | TT-FG1101 | TT | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 900 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
151 | TT-FG1102 | TT | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 700 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
152 | TT-FG1103 | TT | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 700 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
153 | TT-FG1104 | TT | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 600 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
154 | TT-FG1105 | TT | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 620 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
155 | TT-FG1106 | TT | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 520 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
156 | TT-FG1107 | TT | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 590 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
157 | TT-FG1108 | TT | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 480 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
158 | TT-FG1109 | TT | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 520 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
159 | TT-FG1110 | TT | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 430 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
160 | TT-FG1111 | TT | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 450 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
161 | TT-FG1113 | TT | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 430 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
162 | TT-FG1124 | TT | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
163 | TT-FG1125 | TT | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
164 | TT-FG1132 | TT | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
165 | TT-FG1133 | TT | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
166 | TT-FG1152 | TT | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
167 | TT-FA1053-1 | TT | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
168 | TT-FA1053-2 | TT | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
169 | TT-FA1053-3 | TT | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
170 | TT-FA1053-4 | TT | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
171 | TT-FA1053-U | TT | FA1053-U | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
172 | TT-FA1053-V | TT | FA1053-V | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
173 | TT-FA1053-W | TT | FA1053-W | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
174 | TT-FA1072 | TT | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE TRANSMITTER | PD-052 | 0 | 66 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
175 | TT-FA1073 | TT | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE (A) TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
176 | TT-FA1074 | TT | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE (B) TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
177 | TT-FA1076 | TT | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE (A) TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
178 | TT-FA1077 | TT | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE (B) TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
179 | TT-FA1054-1 | TT | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
180 | TT-FA1054-2 | TT | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
181 | TT-FA1054-3 | TT | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
182 | TT-FA1054-4 | TT | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
183 | TT-FA1054-U | TT | FA1054-U | #1 SECONDARY AIR FAN MOTOR WINRING (U) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
184 | TT-FA1054-V | TT | FA1054-V | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
185 | TT-FA1054-W | TT | FA1054-W | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
186 | TT-FA1082 | TT | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE TRANSMITTER TRANSMITTER | PD-053 | 0 | 66 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
187 | TT-FA1083 | TT | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE (A) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
188 | TT-FA1084 | TT | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE (B) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
189 | TT-FA1086 | TT | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE (A) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
190 | TT-FA1087 | TT | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE (B) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
191 | TT-FA1055-A | TT | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 149 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
192 | TT-FA1055-A1 | TT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
193 | TT-FA1055-A2 | TT | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
194 | TT-FA1055-A3 | TT | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
195 | TT-FA1055-A4 | TT | FA1055-A4 | #1 FLUIDIZING AIR BLOWER (A) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
196 | TT-FA1055-AU | TT | FA1055-AU | #1 FLUIDIZING AIR BLOWER (A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
197 | TT-FA1055-AV | TT | FA1055-AV | #1 FLUIDIZING AIR BLOWER (A )MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
198 | TT-FA1055-AW | TT | FA1055-AW | #1 FLUIDIZING AIR BLOWER (A) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
199 | TT-FA1055-B | TT | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 149 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0
200 | TT-FA1055-B1 | TT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
201 | TT-FA1055-B2 | TT | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
202 | TT-FA1055-B3 | TT | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
203 | TT-FA1055-B4 | TT | FA1055-B4 | #1 FLUIDIZING AIR BLOWER (B) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
204 | TT-FA1055-BU | TT | FA1055-BU | #1 FLUIDIZING AIR BLOWER (B) MOTOR WINRING (U) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
205 | TT-FA1055-BV | TT | FA1055-BV | #1 FLUIDIZING AIR BLOWER (B )MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0
206 | TT-FA1055-BW | TT | FA1055-BW | #1 FLUIDIZING AIR BLOWER (B) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0

## TE
ITEM | TAG. NO. | TAG. NO. |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE ( ℃ ) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | TE-P0719-1 | TE | P0719-1 | FIRE PUMP(A) PUMP SIDE BEARING FRONT END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
2 | TE-P0719-2 | TE | P0719-2 | FIRE PUMP(A) PUMP SIDE BEARING REAR END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
3 | TE-P0719-3 | TE | P0719-3 | FIRE PUMP(A) MOTOR SIDE BEARING FRONT END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
4 | TE-P0719-4 | TE | P0719-4 | FIRE PUMP(A) MOTOR SIDE BEARING REAR END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
5 | TE-P0719-U1 | TE | P0719-U1 | FIRE PUMP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
6 | TE-P0719-U2 | TE | P0719-U2 | FIRE PUMP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
7 | TE-P0719-V1 | TE | P0719-V1 | FIRE PUMP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
8 | TE-P0719-V2 | TE | P0719-V2 | FIRE PUMP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
9 | TE-P0719-W1 | TE | P0719-W1 | FIRE PUMP(A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
10 | TE-P0719-W2 | TE | P0719-W2 | FIRE PUMP(A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0
11 | TE-MS1004-1 | TE | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-1 | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
12 | TE-MS1004-2 | TE | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-2 | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
13 | TE-MS1007 | TE | MS1007 | #1 MAIN STEAM TEMPERATURE ELEMENT | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
14 | TE-MS1022-1 | TE | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-011 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
15 | TE-MS1022-2 | TE | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-011 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
16 | TE-CR1004 | TE | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0
17 | TE-CR1005-1 | TE | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0
18 | TE-CR1005-2 | TE | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0
19 | TE-HR1002-1 | TE | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
20 | TE-HR1002-2 | TE | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
21 | TE-HR1004 | TE | HR1004 | #1 REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0
22 | TE-HR1010 | TE | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OUTLET TEMPERATURE ELEMENT | PD-012 | - | - | - | - | FIELD | TT | T/C | PACKAGE (CV) | NEW ADDED | 0
23 | TE-HR1012-1 | TE | HR1012-1 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 15 | 280 | - | - | FIELD | TT | RTD | FHI |  | 0
24 | TE-HR1012-2 | TE | HR1012-2 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 15 | 280 | - | - | FIELD | TT | RTD | FHI |  | 0
25 | TE-TS1011 | TE | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-013 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0
26 | TE-TS1014 | TE | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE ELEMENT | PD-013 | 16 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0
27 | TE-TS1018 | TE | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE ELEMENT | PD-013 | 6.2 | 380 | - | - | FIELD | TT | T/C | FHI |  | 0
28 | TE-TS1023 | TE | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | FIELD | TT | RTD | FHI |  | 0
29 | TE-TS1027 | TE | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | FIELD | TT | T/C | FHI |  | 0
30 | TE-AS1001 | TE | AS1001 | #1 MAIN STEAM DESUPERHEATING DOWNSTREAM TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | FIELD | TT | T/C | FHI |  | 0
31 | TE-AS1003 | TE | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | FIELD | TT | T/C | FHI |  | 0
32 | TE-AS1015 | TE | AS1015 | #1 GLAND STEAM DESUPERHEATING OUTLET TEMPERATURE ELEMENT | PD-014 | 13 | 300 | - | - | FIELD | TT | T/C | FHI |  | 0
33 | TE-SB1056 | TE | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0
34 | TE-SB1057 | TE | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0
35 | TE-CD1101 | TE | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0
36 | TE-CD1102 | TE | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | FIELD | TT | RTD | FHI |  | 0
37 | TE-CD1103-1 | TE | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | FIELD | TT | RTD | FHI |  | 0
38 | TE-CD1103-2 | TE | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | FIELD | TT | RTD | FHI |  | 0
39 | TE-CD1104 | TE | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE ELEMENT | PD-016 | 8 | 170 | - | - | FIELD | TT | RTD | FHI |  | 0
40 | TE-CD1110-1 | TE | CD1110-1 | #1 CONDENSER HOT WELL STEAM TEMPERATURE ELEMENT-1 | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0
41 | TE-CD1110-2 | TE | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE ELEMENT-2 | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0
42 | TE-CD1110-3 | TE | CD1110-3 | #1 CONDENSER NECK TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0
43 | TE-CD1110-4 | TE | CD1110-4 | #1 CONDENSER FLASH CHAMBER TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0
44 | TE-CD1116-A1 | TE | CD1116-A1 | #1 CONDENSAT PUMP (A) COUPLING TEMPERATURE ELEMENT | PD-016 | - | - | 0~120 | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
45 | TE-CD1116-A3 | TE | CD1116-A3 | #1 CONDENSAT PUMP (A) MOTOR BEARING DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
46 | TE-CD1116-A4 | TE | CD1116-A4 | #1 CONDENSAT PUMP (A) MOTOR BEARING NON-DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
47 | TE-CD1116-AU1 | TE | CD1116-AU1 | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
48 | TE-CD1116-AU2 | TE | CD1116-AU2 | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
49 | TE-CD1116-AV1 | TE | CD1116-AV1 | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
50 | TE-CD1116-AV2 | TE | CD1116-AV2 | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
51 | TE-CD1116-AW1 | TE | CD1116-AW1 | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
52 | TE-CD1116-AW2 | TE | CD1116-AW2 | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
53 | TE-CD1116-B1 | TE | CD1116-B1 | #1 CONDENSAT PUMP (B) COUPLING TEMPERATURE ELEMENT | PD-016 | - | - | 0~120 | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
54 | TE-CD1116-B3 | TE | CD1116-B3 | #1 CONDENSAT PUMP (B) MOTOR BEARING DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
55 | TE-CD1116-B4 | TE | CD1116-B4 | #1 CONDENSAT PUMP (B) MOTOR BEARING NON-DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
56 | TE-CD1116-BU1 | TE | CD1116-BU1 | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
57 | TE-CD1116-BU2 | TE | CD1116-BU2 | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
58 | TE-CD1116-BV1 | TE | CD1116-BV1 | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
59 | TE-CD1116-BV2 | TE | CD1116-BV2 | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
60 | TE-CD1116-BW1 | TE | CD1116-BW1 | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
61 | TE-CD1116-BW2 | TE | CD1116-BW2 | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0
62 | TE-CD1118 | TE | CD1118 | #1 CONDENSATE WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0
63 | TE-CD1119 | TE | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0
64 | TE-CD1120 | TE | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0
65 | TE-CD1122 | TE | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | FIELD | TT | RTD | FHI |  | 0
66 | TE-FW1010 | TE | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 10 | 180 | - | - | FIELD | TT | RTD | FHI |  | 0
67 | TE-FW1011 | TE | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE ELEMENT | PD-017 | 230 | 180 | - | - | FIELD | TT | RTD | FHI |  | 0
68 | TE-FW1105 | TE | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 220 | - | - | FIELD | TT | RTD | FHI |  | 0
69 | TE-FW1106 | TE | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 275 | - | - | FIELD | TT | RTD | FHI |  | 0
70 | TE-FW1115-A1 | TE | FW1115-A1 | #1 BFP(A) PUMP SIDE BEARING FRONT(NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0
71 | TE-FW1115-A2 | TE | FW1115-A2 | #1 BFP(A) PUMP BEARING REAR(DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0
72 | TE-FW1115-A3 | TE | FW1115-A3 | #1 BFP(A) MOTOR SIDE BEARING REAR (DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
73 | TE-FW1115-A4 | TE | FW1115-A4 | #1 BFP(A) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
74 | TE-FW1115-AU1 | TE | FW1115-AU1 | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
75 | TE-FW1115-AU2 | TE | FW1115-AU2 | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
76 | TE-FW1115-AV1 | TE | FW1115-AV1 | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
77 | TE-FW1115-AV2 | TE | FW1115-AV2 | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
78 | TE-FW1115-AW1 | TE | FW1115-AW1 | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
79 | TE-FW1115-AW2 | TE | FW1115-AW2 | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
80 | TE-FW1115-B1 | TE | FW1115-B1 | #1 BFP(B) PUMP BEARING FRONT(NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0
81 | TE-FW1115-B2 | TE | FW1115-B2 | #1 BFP(B) PUMP BEARING REAR(DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0
82 | TE-FW1115-B3 | TE | FW1115-B3 | #1 BFP(B) MOTOR SIDE BEARING REAR (DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
83 | TE-FW1115-B4 | TE | FW1115-B4 | #1 BFP(B) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
84 | TE-FW1115-BU-1 | TE | FW1115-BU-1 | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
85 | TE-FW1115-BU-2 | TE | FW1115-BU-2 | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-017 |  |  | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
86 | TE-FW1115-BV-1 | TE | FW1115-BV-1 | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
87 | TE-FW1115-BV-2 | TE | FW1115-BV-2 | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-017 |  |  | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
88 | TE-FW1115-BW-1 | TE | FW1115-BW-1 | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
89 | TE-FW1115-BW-2 | TE | FW1115-BW-2 | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0
90 | TE-HD1102 | TE | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 150 | - | - | FIELD | TT | RTD | FHI |  | 0
91 | TE-HD1103 | TE | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 200 | - | - | FIELD | TT | RTD | FHI |  | 0
92 | TE-HD1105 | TE | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE ELEMENT | PD-018 | 16 & Full Vaccum | 210 | - | - | FIELD | TT | RTD | FHI |  | 0
93 | TE-HD1106 | TE | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 45 & Full Vaccum | 260 | - | - | FIELD | TT | RTD | FHI |  | 0
94 | TE-BR1020 | TE | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0
95 | TE-BR1030 | TE | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0
96 | TE-BR1040 | TE | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0
97 | TE-BR1110 | TE | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0
98 | TE-BR1120-1 | TE | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-1 | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0
99 | TE-BR1120-2 | TE | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-2 | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0
100 | TE-BR1130-1 | TE | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0
101 | TE-BR1130-2 | TE | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0
102 | TE-BR1140-1 | TE | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0
103 | TE-BR1140-2 | TE | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0
104 | TE-BR1150-1 | TE | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0
105 | TE-BR1150-2 | TE | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0
106 | TE-FW1160 | TE | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 230 | 275 | - | - | FIELD | TT | RTD | FHI |  | 0
107 | TE-SW1110-A1 | TE | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0
108 | TE-SW1110-A2 | TE | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0
109 | TE-SW1110-B1 | TE | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0
110 | TE-SW1110-B2 | TE | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0
111 | TE-SW1501-A31 | TE | SW1501-A31 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
112 | TE-SW1501-A32 | TE | SW1501-A32 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
113 | TE-SW1501-A41 | TE | SW1501-A41 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
114 | TE-SW1501-A42 | TE | SW1501-A42 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
115 | TE-SW1501-AU1 | TE | SW1501-AU1 | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
116 | TE-SW1501-AU2 | TE | SW1501-AU2 | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
117 | TE-SW1501-AV1 | TE | SW1501-AV1 | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
118 | TE-SW1501-AV2 | TE | SW1501-AV2 | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
119 | TE-SW1501-AW1 | TE | SW1501-AW1 | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
120 | TE-SW1501-AW2 | TE | SW1501-AW2 | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
121 | TE-SW1501-B31 | TE | SW1501-B31 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
122 | TE-SW1501-B32 | TE | SW1501-B32 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
123 | TE-SW1501-B41 | TE | SW1501-B41 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
124 | TE-SW1501-B42 | TE | SW1501-B42 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
125 | TE-SW1501-BU1 | TE | SW1501-BU1 | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
126 | TE-SW1501-BU2 | TE | SW1501-BU2 | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
127 | TE-SW1501-BV1 | TE | SW1501-BV1 | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
128 | TE-SW1501-BV2 | TE | SW1501-BV2 | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
129 | TE-SW1501-BW1 | TE | SW1501-BW1 | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
130 | TE-SW1501-BW2 | TE | SW1501-BW2 | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
131 | TE-SW1501-C31 | TE | SW1501-C31 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
132 | TE-SW1501-C32 | TE | SW1501-C32 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
133 | TE-SW1501-C41 | TE | SW1501-C41 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
134 | TE-SW1501-C42 | TE | SW1501-C42 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
135 | TE-SW1501-CU1 | TE | SW1501-CU1 | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
136 | TE-SW1501-CU2 | TE | SW1501-CU2 | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
137 | TE-SW1501-CV1 | TE | SW1501-CV1 | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
138 | TE-SW1501-CV2 | TE | SW1501-CV2 | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
139 | TE-SW1501-CW1 | TE | SW1501-CW1 | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
140 | TE-SW1501-CW2 | TE | SW1501-CW2 | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0
141 | TE-CW1108-A3 | TE | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR BEARING TEMPERATURE-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
142 | TE-CW1108-A4 | TE | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR BEARING TEMPERATURE-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
143 | TE-CW1108-AU1 | TE | CW1108-AU1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
144 | TE-CW1108-AU2 | TE | CW1108-AU2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
145 | TE-CW1108-AV1 | TE | CW1108-AV1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
146 | TE-CW1108-AV2 | TE | CW1108-AV2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
147 | TE-CW1108-AW1 | TE | CW1108-AW1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
148 | TE-CW1108-AW2 | TE | CW1108-AW2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
149 | TE-CW1108-B3 | TE | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR BEARING TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
150 | TE-CW1108-B4 | TE | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR BEARING TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
151 | TE-CW1108-BU1 | TE | CW1108-BU1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
152 | TE-CW1108-BU2 | TE | CW1108-BU2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
153 | TE-CW1108-BV1 | TE | CW1108-BV1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
154 | TE-CW1108-BV2 | TE | CW1108-BV2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
155 | TE-CW1108-BW1 | TE | CW1108-BW1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
156 | TE-CW1108-BW2 | TE | CW1108-BW2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0
157 | TE-CW1152 | TE | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0
158 | TE-CW1153 | TE | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0
159 | TE-FG1009-A | TE | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
160 | TE-FG1009-B | TE | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
161 | TE-FG1057-8 | TE | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | - | PACKAGE (CEMS) |  | 0
162 | TE-FG1090-A | TE | FG1090-A | #1 FURNACE FRONT TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
163 | TE-FG1090-B | TE | FG1090-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
164 | TE-FG1090-C | TE | FG1090-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
165 | TE-FG1090-D | TE | FG1090-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
166 | TE-FG1090-E | TE | FG1090-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
167 | TE-FG1090-F | TE | FG1090-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
168 | TE-FG1090-G | TE | FG1090-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
169 | TE-FG1090-H | TE | FG1090-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
170 | TE-FG1090-I | TE | FG1090-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
171 | TE-FG1091-A | TE | FG1091-A | #1 FURNACE FRONT TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
172 | TE-FG1091-B | TE | FG1091-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
173 | TE-FG1091-C | TE | FG1091-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
174 | TE-FG1091-D | TE | FG1091-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
175 | TE-FG1091-E | TE | FG1091-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
176 | TE-FG1091-F | TE | FG1091-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
177 | TE-FG1091-G | TE | FG1091-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
178 | TE-FG1091-H | TE | FG1091-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
179 | TE-FG1091-I | TE | FG1091-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
180 | TE-FG1092-A | TE | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
181 | TE-FG1092-B | TE | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
182 | TE-FG1095-A | TE | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
183 | TE-FG1095-B | TE | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
184 | TE-FG1096-A | TE | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
185 | TE-FG1096-B | TE | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0
186 | TE-FG1100 | TE | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | FIELD | TT | T/C | FHI |  | 0
187 | TE-FG1101 | TE | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | FIELD | TT | T/C | FHI |  | 0
188 | TE-FG1102 | TE | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | FIELD | TT | T/C | FHI |  | 0
189 | TE-FG1103 | TE | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | FIELD | TT | T/C | FHI |  | 0
190 | TE-FG1104 | TE | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 600 | - | - | FIELD | TT | T/C | FHI |  | 0
191 | TE-FG1105 | TE | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 620 | - | - | FIELD | TT | T/C | FHI |  | 0
192 | TE-FG1106 | TE | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | FIELD | TT | T/C | FHI |  | 0
193 | TE-FG1107 | TE | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 590 | - | - | FIELD | TT | T/C | FHI |  | 0
194 | TE-FG1108 | TE | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 480 | - | - | FIELD | TT | T/C | FHI |  | 0
195 | TE-FG1109 | TE | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | FIELD | TT | T/C | FHI |  | 0
196 | TE-FG1110 | TE | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE ELEMENT-A | PD-051 | ±890mmH2O | 430 | - | - | FIELD | TT | T/C | FHI |  | 0
197 | TE-FG1111 | TE | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 450 | - | - | FIELD | TT | T/C | FHI |  | 0
198 | TE-FG1113 | TE | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE ELEMENT-B | PD-051 | ±890mmH2O | 430 | - | - | FIELD | TT | T/C | FHI |  | 0
199 | TE-FG1124 | TE | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 371 | - | - | FIELD | TT | T/C | FHI |  | 0
200 | TE-FG1125 | TE | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(B) | PD-051 | ±890mmH2O | 371 | - | - | FIELD | TT | T/C | FHI |  | 0
201 | TE-FG1132 | TE | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | RTD | FHI |  | 0
202 | TE-FG1133 | TE | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | RTD | FHI |  | 0
203 | TE-FG1152 | TE | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | T/C | FHI |  | 0
204 | TE-FA1072 | TE | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-052 | 0 | 66 | - | - | FIELD | TT | T/C | FHI |  | 0
205 | TE-FA1073 | TE | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0
206 | TE-FA1074 | TE | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-052 | -340~2500 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0
207 | TE-FA1076 | TE | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0
208 | TE-FA1077 | TE | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-052 | -340~2500 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0
209 | TE-FA1082 | TE | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-053 | 0 | 66 | - | - | FIELD | TT | T/C | FHI |  | 0
210 | TE-FA1083 | TE | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0
211 | TE-FA1084 | TE | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0
212 | TE-FA1086 | TE | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0
213 | TE-FA1087 | TE | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0
214 | TE-FA1055-A | TE | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | FIELD | TT | T/C | FHI |  | 0
215 | TE-FA1055-B | TE | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | FIELD | TT | T/C | FHI |  | 0

## TG
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE ( ℃ ) | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | TG-MS1005 | TG | MS1005 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE GAUGE | PD-011 | 144 | 550 | 0~700 | - | - | - | BI-METAL | FHI |  | 0
2 | TG-TS1012 | TG | TS1012 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE GAUGE | PD-013 | 45 | 395 | 0~600 | - | - | - | BI-METAL | FHI |  | 0
3 | TG-TS1016 | TG | TS1016 | #1 EXTRACTION STEAM NO.2 TEMPERATURE GAUGE | PD-013 | 16 | 440 | 0~600 | - | - | - | BI-METAL | FHI |  | 0
4 | TG-TS1021 | TG | TS1021 | #1 DEAERATOR INLET STEAM TEMPERATURE GAUGE | PD-013 | 6.2 | 380 | 0~500 | - | - | - | BI-METAL | FHI |  | 0
5 | TG-TS1025 | TG | TS1025 | #1 EXTRACTION STEAM NO.4 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | 0~300 | - | - | - | BI-METAL | FHI |  | 0
6 | TG-TS1029 | TG | TS1029 | #1 EXTRACTION STEAM NO.5 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | 0~300 | - | - | - | BI-METAL | FHI |  | 0
7 | TG-AS1002 | TG | AS1002 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE GAUGE | PD-014 | 13 | 390 | 0~600 | - | - | - | BI-METAL | FHI |  | 0
8 | TG-AS1016 | TG | AS1016 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE GAUGE | PD-014 | 13 | 300 | 0~500 | - | - | - | BI-METAL | FHI |  | 0
9 | TG-CD1119-1 | TG | CD1119-1 | #1 STEAM JET AIR EJECTOR CONDENSER COOLING WATER INLET TEMPERATURE GAUGE | PD-014 | - | 44 | 0~100 | - | - | - | - | PACKAGE (AIR EJECTOR) | NEW ADDED | 0
10 | TG-CD1119-2 | TG | CD1119-2 | #1 STEAM JET AIR EJECTOR CONDENSER COOLING WATER OUTLET TEMPERATURE GAUGE | PD-014 | - | 49.5 | 0~100 | - | - | - | - | PACKAGE (AIR EJECTOR) | NEW ADDED | 0
11 | TG-SB1055 | TG | SB1055 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | 0~500 | - | - | - | BI-METAL | FHI |  | 0
12 | TG-SB1058 | TG | SB1058 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | 0~500 | - | - | - | BI-METAL | FHI |  | 0
13 | TG-CD1104-1 | TG | CD1104-1 | #1 DEAERATOR TEMPERATURE GAUGE | PD-016 | 8 | 380 | 0~400 | - | - | - | BI-METAL | FHI |  | 0
14 | TG-CD1104-2 | TG | CD1104-2 | #1 DEAERATOR STORAGE TANK TEMPERATURE GAUGE | PD-016 | 8 | 170 | 0~200 | - | - | - | BI-METAL | FHI |  | 0
15 | TG-CD1110-1 | TG | CD1110-1 | #1 CONDENSER HOT WELL WATER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | 0~200 | - | - | - | BI-METAL | FHI |  | 0
16 | TG-CD1110-2 | TG | CD1110-2 | #1 CONDENSER FLASH CHAMBER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | 0~200 | - | - | - | BI-METAL | FHI |  | 0
17 | TG-CD1118 | TG | CD1118 | #1 CONDENSATE WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
18 | TG-CD1119 | TG | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
19 | TG-CD1120 | TG | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
20 | TG-FW1115-A1 | TG | FW1115-A1 | #1 BFP(A) PUMP DISCHARGE TEMPERATURE GAUGE | PD-017 | - | - | 0~300 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
21 | TG-FW1115-A2 | TG | FW1115-A2 | #1 BFP(A) PLAN 23 FLUSHING IN LINE DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
22 | TG-FW1115-A3 | TG | FW1115-A3 | #1 BFP(A) PLAN 23 FLUSHING IN LINE NON DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
23 | TG-FW1115-A4 | TG | FW1115-A4 | #1 BFP(A) PUMP DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
24 | TG-FW1115-A5 | TG | FW1115-A5 | #1 BFP(A) PUMP NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
25 | TG-FW1115-A6 | TG | FW1115-A6 | #1 BFP(A) MOTOR DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
26 | TG-FW1115-A7 | TG | FW1115-A7 | #1 BFP(A) MOTOR NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
27 | TG-FW1115-A8 | TG | FW1115-A8 | #1 BFP(A) COOLING WATER OUTLET HEADER TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
28 | TG-FW1115-B1 | TG | FW1115-B1 | #1 BFP(B) PUMP DISCHARGE TEMPERATURE GAUGE | PD-017 | - | - | 0~300 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
29 | TG-FW1115-B2 | TG | FW1115-B2 | #1 BFP(B) PLAN 23 FLUSHING IN LINE DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
30 | TG-FW1115-B3 | TG | FW1115-B3 | #1 BFP(B) PLAN 23 FLUSHING IN LINE NON DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
31 | TG-FW1115-B4 | TG | FW1115-B4 | #1 BFP(B) PUMP DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
32 | TG-FW1115-B5 | TG | FW1115-B5 | #1 BFP(B) PUMP NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
33 | TG-FW1115-B6 | TG | FW1115-B6 | #1 BFP(B) MOTOR DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
34 | TG-FW1115-B7 | TG | FW1115-B7 | #1 BFP(B) MOTOR NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
35 | TG-FW1115-B8 | TG | FW1115-B8 | #1 BFP(B) COOLING WATER OUTLET HEADER TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0
36 | TG-LO1115-A1 | TG | LO1115-A1 | #1 BFP(A) LUBE OIL COOLER INLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0
37 | TG-LO1115-A2 | TG | LO1115-A2 | #1 BFP(A) LUBE OIL COOLER OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0
38 | TG-LO1115-A3 | TG | LO1115-A3 | #1 BFP(A) LUBE OIL TANK TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0
39 | TG-LO1115-B1 | TG | LO1115-B1 | #1 BFP(B) LUBE OIL COOLER INLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0
40 | TG-LO1115-B2 | TG | LO1115-B2 | #1 BFP(B) LUBE OIL COOLER OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0
41 | TG-LO1115-B3 | TG | LO1115-B3 | #1 BFP(B) LUBE OIL TANK TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0
42 | TG-HD1102 | TG | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 150 | 0~200 | - | - | - | BI-METAL | FHI |  | 0
43 | TG-HD1103 | TG | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 200 | 0~200 | - | - | - | BI-METAL | FHI |  | 0
44 | TG-HD1105 | TG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | 0~300 | - | - | - | BI-METAL | FHI |  | 0
45 | TG-HD1106 | TG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | 0~300 | - | - | - | BI-METAL | FHI |  | 0
46 | TG-FW1160 | TG | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE GAUGE | PD-019 | 230 | 275 | 0~400 | - | - | - | BI-METAL | FHI |  | 0
47 | TG-SW1107-A | TG | SW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
48 | TG-SW1107-B | TG | SW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
49 | TG-SW1107-C | TG | SW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
50 | TG-SW1110-A1 | TG | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
51 | TG-SW1110-A2 | TG | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
52 | TG-SW1110-B1 | TG | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
53 | TG-SW1110-B2 | TG | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
54 | TG-SW1503-A | TG | SW1503-A | #1 SEAWATER BOOSTER PUMP A SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
55 | TG-SW1503-B | TG | SW1503-B | #1 SEAWATER BOOSTER PUMP B SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
56 | TG-SW1503-C | TG | SW1503-C | #1 SEAWATER BOOSTER PUMP C SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
57 | TG-SW1551 | TG | SW1551 | #1 SEAWATER PUMP DISCHARGE HEADER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
58 | TG-SW1552 | TG | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
59 | TG-CW1107-A | TG | CW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
60 | TG-CW1107-B | TG | CW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
61 | TG-CW1107-C | TG | CW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
62 | TG-CW1115-A1 | TG | CW1115-A1 | #1 BFP MOTOR P-1115A COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
63 | TG-CW1115-B1 | TG | CW1115-B1 | #1 BFP MOTOR P-1115B COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
64 | TG-CW1151 | TG | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
65 | TG-CW1152 | TG | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
66 | TG-CW1154-A1 | TG | CW1154-A1 | #1 STEAM TURBINE LUBE OIL COOLER A INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
67 | TG-CW1154-A2 | TG | CW1154-A2 | #1 STEAM TURBINE LUBE OIL COOLER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
68 | TG-CW1154-B1 | TG | CW1154-B1 | #1 STEAM TURBINE LUBE OIL COOLER B INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
69 | TG-CW1154-B2 | TG | CW1154-B2 | #1 STEAM TURBINE LUBE OIL COOLER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
70 | TG-CW1155-A1 | TG | CW1155-A1 | #1 GENERATOR AIR COOLER A-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
71 | TG-CW1155-A2 | TG | CW1155-A2 | #1 GENERATOR AIR COOLER A-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
72 | TG-CW1155-A3 | TG | CW1155-A3 | #1 GENERATOR AIR COOLER A-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
73 | TG-CW1155-A4 | TG | CW1155-A4 | #1 GENERATOR AIR COOLER A-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
74 | TG-CW1155-B1 | TG | CW1155-B1 | #1 GENERATOR AIR COOLER B-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
75 | TG-CW1155-B2 | TG | CW1155-B2 | #1 GENERATOR AIR COOLER B-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
76 | TG-CW1155-B3 | TG | CW1155-B3 | #1 GENERATOR AIR COOLER B-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
77 | TG-CW1155-B4 | TG | CW1155-B4 | #1 GENERATOR AIR COOLER B-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
78 | TG-CW1155-C1 | TG | CW1155-C1 | #1 GENERATOR AIR COOLER C INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
79 | TG-CW1155-C2 | TG | CW1155-C2 | #1 GENERATOR AIR COOLER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
80 | TG-CW1155-D1 | TG | CW1155-D1 | #1 GENERATOR AIR COOLER D INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
81 | TG-CW1155-D2 | TG | CW1155-D2 | #1 GENERATOR AIR COOLER D OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
82 | TG-DO0003 | TG | DO0003 | DIESEL OIL PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
83 | TG-DO1006 | TG | DO1006 | #1 DIESEL OIL TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
84 | TG-PA0151 | TG | PA0151 | PA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-1/6 | 10 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
85 | TG-IA0151 | TG | IA0151 | IA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-2/6 | 10 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0
86 | TG-CW1140-3 | TG | CW1140-3 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY THERMOMETER | PD-044 | 5 | 40 | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
87 | TG-SP1001 | TG | SP1001 | #1 DEAERATOR UPSTREAM THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
88 | TG-SP1002 | TG | SP1002 | #1 DEAERATOR OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
89 | TG-SP1003 | TG | SP1003 | #1 MAKE-UP WATER PUMP OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
90 | TG-SP1004 | TG | SP1004 | #1 ECONOMIZER INLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
91 | TG-SP1005 | TG | SP1005 | #1 DRUM WATER (BLOW DOWN) PRESSUE GAUGE | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
92 | TG-SP1006 | TG | SP1006 | #1 SATURATED STEAM THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
93 | TG-SP1007 | TG | SP1007 | #1 MAIN STEAM LINE THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
94 | TG-SP1008 | TG | SP1008 | #1 CONDENSATE PUMP OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0
95 | TG-CD1116-A | TG | CD1116-A | #1 CONDENSATE PUMP (A) COUPLING TEMPERATURE DAUGE | PD-016 | - | - | later | - | - | - | - | PACKAGE (CONDENSATE PUMP) | DELETED | 0
96 | TG-CD1116-B | TG | CD1116-B | #1 CONDENSATE PUMP (B) COUPLING TEMPERATURE DAUGE | PD-016 | - | - | later | - | - | - | - | PACKAGE (CONDENSATE PUMP) | DELETED | 0

## TW
ITEM | TAG. NO. | TAG. NO. |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | TW-CR1603 | TW | CR1603 | #1 TEST WELL AT COLD REHEAT LINE B | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0
2 | TW-CR1605-1 | TW | CR1605-1 | #1 TEST WELL AT COLD REHEATER COMMON HEADER -1 | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0
3 | TW-CR1605-2 | TW | CR1605-2 | #1 TEST WELL AT COLD REHEATER COMMON HEADER -2 | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0
4 | TW-MS1004-1 | TW | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
5 | TW-MS1004-2 | TW | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
6 | TW-MS1005 | TW | MS1005 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE GAUGE | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
7 | TW-MS1007 | TW | MS1007 | #1 MAIN STEAM TEMPERATURE ELEMENT | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
8 | TW-MS1022-1 | TW | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-011 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
9 | TW-MS1022-2 | TW | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-011 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
10 | TW-MS1602-1 | TW | MS1602-1 | #1 TEST WELL AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
11 | TW-MS1602-2 | TW | MS1602-2 | #1 TEST WELL AT MAIN STEAM LINE-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
12 | TW-MS1604 | TW | MS1604 | #1 TEST WELL AT TURBINE LEADING LINE A | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
13 | TW-MS1606 | TW | MS1606 | #1 TEST WELL AT TURBINE LEADING LINE B | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
14 | TW-MS1607 | TW | MS1607 | #1 TEST WELL AT HP TURBINE BYPASS OUTLET | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0
15 | TW-MS1902-1 | TW | MS1902-1 | #1 THERMOWELL WELL FOR TE-MS1902-1 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
16 | TW-MS1902-2 | TW | MS1902-2 | #1 THERMOWELL WELL FOR TE-MS1902-2 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
17 | TW-MS1902-3 | TW | MS1902-3 | #1 THERMOWELL WELL FOR TE-MS1902-3 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
18 | TW-MS1902-4 | TW | MS1902-4 | #1 THERMOWELL WELL FOR TE-MS1902-4 AT MAIN INLET STEAM LINE-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0
19 | TW-CR1004 | TW | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0
20 | TW-CR1005-1 | TW | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0
21 | TW-CR1005-2 | TW | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0
22 | TW-HR1002-1 | TW | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
23 | TW-HR1002-2 | TW | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
24 | TW-HR1004 | TW | HR1004 | #1 REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0
25 | TW-HR1010 | TW | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OUTLET TEMPERATURE ELEMENT | PD-012 | - | - | - | - | - | - | - | PACKAGE (CV) | NEW ADDED | 0
26 | TW-HR1012-1 | TW | HR1012-1 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 15 | 280 | - | - | - | - | - | FHI | NEW ADDED | 0
27 | TW-HR1012-2 | TW | HR1012-2 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 15 | 280 | - | - | - | - | - | FHI | NEW ADDED | 0
28 | TW-HR1603-1 | TW | HR1603-1 | #1 TEST WELL AT HOT REHEATER COMMON -1 | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0
29 | TW-HR1603-2 | TW | HR1603-2 | #1 TEST WELL AT HOT REHEATER COMMON -2 | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0
30 | TW-HR1605 | TW | HR1605 | #1 TEST WELL AT ILP TURBINE LEADING LINE A | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0
31 | TW-HR1607 | TW | HR1607 | #1 TEST WELL AT ILP TURBINE LEADING LINE B | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0
32 | TW-HR1608 | TW | HR1608 | #1 TEST WELL AT LP TURBINE BYPASS OUTLET | PD-012 | 15 | 280 | - | - | - | - | - | FHI |  | 0
33 | TW-HR1902 | TW | HR1902 | #1 HOT REHEAT STEAM TEMPERATURE | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0
34 | TW-HR1902 | TW | HR1902 | #1 THERMOWELL WELL FOR TE-MS1902 AT ILP TURBINE LEADING LINE A | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0
35 | TW-TS1011 | TW | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-013 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0
36 | TW-TS1012 | TW | TS1012 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE GAUGE | PD-013 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0
37 | TW-TS1014 | TW | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE ELEMENT | PD-013 | 16 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0
38 | TW-TS1016 | TW | TS1016 | #1 EXTRACTION STEAM NO.2 TEMPERATURE GAUGE | PD-013 | 16 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0
39 | TW-TS1018 | TW | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE ELEMENT | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0
40 | TW-TS1021 | TW | TS1021 | #1 DEAERATOR INLET STEAM TEMPERATURE GAUGE | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0
41 | TW-TS1023 | TW | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0
42 | TW-TS1025 | TW | TS1025 | #1 EXTRACTION STEAM NO.4 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0
43 | TW-TS1027 | TW | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0
44 | TW-TS1029 | TW | TS1029 | #1 EXTRACTION STEAM NO.5 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0
45 | TW-TS1602 | TW | TS1602 | #1 TEST WELL AT COLD REHEATER TO #2 HIGH PRESSURE HEATER | PD-013 | 45 | 395 | - | - | - | - | - | FHI |  | 0
46 | TW-TS1604 | TW | TS1604 | #1 TEST WELL AT EXTRACTION STEAM NO.2 LINE | PD-013 | 16 | 440 | - | - | - | - | - | FHI |  | 0
47 | TW-TS1606 | TW | TS1606 | #1 TEST WELL AT EXTRACTION STEAM NO.3 LINE | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI |  | 0
48 | TW-AS1001 | TW | AS1001 | #1 MAIN STEAM DESUPERHEATING DOWNSTREAM TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0
49 | TW-AS1002 | TW | AS1002 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE GAUGE | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0
50 | TW-AS1003 | TW | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0
51 | TW-AS1015 | TW | AS1015 | #1 GLAND STEAM DESUPERHEATING OUTLET TEMPERATURE ELEMENT | PD-014 | 13 | 300 | - | - | - | - | - | FHI | NEW ADDED | 0
52 | TW-AS1016 | TW | AS1016 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE GAUGE | PD-014 | 13 | 300 | - | - | - | - | - | FHI | NEW ADDED | 0
53 | TW-SB1055 | TW | SB1055 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0
54 | TW-SB1056 | TW | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0
55 | TW-SB1057 | TW | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0
56 | TW-SB1058 | TW | SB1058 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0
57 | TW-CD1101 | TW | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
58 | TW-CD1102 | TW | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | - | - | - | FHI | NEW ADDED | 0
59 | TW-CD1103-1 | TW | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | - | - | - | FHI | NEW ADDED | 0
60 | TW-CD1103-2 | TW | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | - | - | - | FHI | NEW ADDED | 0
61 | TW-CD1104 | TW | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE ELEMENT | PD-016 | 8 | 170 | - | - | - | - | - | FHI | NEW ADDED | 0
62 | TW-CD1104-1 | TW | CD1104-1 | #1 DEAERATOR TEMPERATURE GAUGE | PD-016 | 8 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0
63 | TW-CD1104-2 | TW | CD1104-2 | #1 DEAERATOR STORAGE TANK TEMPERATURE GAUGE | PD-016 | 8 | 170 | - | - | - | - | - | FHI | NEW ADDED | 0
64 | TW-CD1110-1 | TW | CD1110-1 | #1 CONDENSER HOT WELL STEAM TEMPERATURE ELEMENT-1 | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0
65 | TW-CD1110-1(G) | TW | CD1110-1(G) | #1 CONDENSER HOT WELL WATER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | - | - | - | - | - | FHI | NEW ADDED | 0
66 | TW-CD1110-2 | TW | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE ELEMENT-2 | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0
67 | TW-CD1110-2(G) | TW | CD1110-2(G) | #1 CONDENSER FLASH CHAMBER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | - | - | - | - | - | FHI | NEW ADDED | 0
68 | TW-CD1110-3 | TW | CD1110-3 | #1 CONDENSER NECK TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0
69 | TW-CD1110-4 | TW | CD1110-4 | #1 CONDENSER FLASH CHAMBER TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0
70 | TW-CD1118 | TW | CD1118 | #1 CONDENSATE WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
71 | TW-CD1118(G) | TW | CD1118(G) | #1 CONDENSATE WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
72 | TW-CD1119 | TW | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
73 | TW-CD1119(G) | TW | CD1119(G) | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
74 | TW-CD1120 | TW | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
75 | TW-CD1120(G) | TW | CD1120(G) | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
76 | TW-CD1122 | TW | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | - | - | - | FHI | NEW ADDED | 0
77 | TW-CD1603 | TW | CD1603 | #1 TEST WELL AT CONDENSATE PUMP COMMON DISCHARGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0
78 | TW-CD1604 | TW | CD1604 | #1 TEST WELL AT GLAND STEAM CONDENSER OUTLET | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0
79 | TW-CD1605 | TW | CD1605 | #1 TEST WELL AT LOW PRESSURE HEATER NO.1 INLET CONDENSATE SIDE | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0
80 | TW-CD1607 | TW | CD1607 | #1 TEST WELL AT DEAERATOR INLET CONDENSATE-1 | PD-016 | 24 | 200 | - | - | - | - | - | FHI |  | 0
81 | TW-CD1608 | TW | CD1608 | #1 TEST WELL AT DEAERATOR INLET CONDENSATE-2 | PD-016 | 24 | 200 | - | - | - | - | - | FHI |  | 0
82 | TW-FW1010 | TW | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 10 | 180 | - | - | - | - | - | FHI | NEW ADDED | 0
83 | TW-FW1011 | TW | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE ELEMENT | PD-017 | 230 | 180 | - | - | - | - | - | FHI | NEW ADDED | 0
84 | TW-FW1105 | TW | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 220 | - | - | - | - | - | FHI | NEW ADDED | 0
85 | TW-FW1106 | TW | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0
86 | TW-FW1601 | TW | FW1601 | #1 TEST WELL AT BFP INLET | PD-017 | 10 | 180 | - | - | - | - | - | FHI |  | 0
87 | TW-FW1602 | TW | FW1602 | #1 TEST WELL AT BFP INLET | PD-017 | 10 | 180 | - | - | - | - | - | FHI |  | 0
88 | TW-FW1604 | TW | FW1604 | #1 TEST WELL AT BFP COMMON DISCHARGE | PD-017 | 230 | 180 | - | - | - | - | - | FHI |  | 0
89 | TW-FW1605 | TW | FW1605 | #1 TEST WELL AT BFP COMMON DISCHARGE | PD-017 | 230 | 180 | - | - | - | - | - | FHI |  | 0
90 | TW-FW1606 | TW | FW1606 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER | PD-017 | 230 | 220 | - | - | - | - | - | FHI |  | 0
91 | TW-FW1607 | TW | FW1607 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER | PD-017 | 230 | 220 | - | - | - | - | - | FHI |  | 0
92 | TW-FW1609 | TW | FW1609 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER | PD-017 | 230 | 275 | - | - | - | - | - | FHI |  | 0
93 | TW-FW1610 | TW | FW1610 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER | PD-017 | 230 | 275 | - | - | - | - | - | FHI |  | 0
94 | TW-HD1102 | TW | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 150 | - | - | - | - | - | FHI | NEW ADDED | 0
95 | TW-HD1102(G) | TW | HD1102(G) | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 150 | - | - | - | - | - | FHI | NEW ADDED | 0
96 | TW-HD1103 | TW | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 200 | - | - | - | - | - | FHI | NEW ADDED | 0
97 | TW-HD1103(G) | TW | HD1103(G) | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 200 | - | - | - | - | - | FHI | NEW ADDED | 0
98 | TW-HD1105 | TW | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE ELEMENT | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI | NEW ADDED | 0
99 | TW-HD1105(G) | TW | HD1105(G) | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI | NEW ADDED | 0
100 | TW-HD1106 | TW | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI | NEW ADDED | 0
101 | TW-HD1106(G) | TW | HD1106(G) | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI | NEW ADDED | 0
102 | TW-HD1601 | TW | HD1601 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 DRAIN LINE | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI |  | 0
103 | TW-HD1602 | TW | HD1602 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 DRAIN LINE | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI |  | 0
104 | TW-BR1020 | TW | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0
105 | TW-BR1030 | TW | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0
106 | TW-BR1040 | TW | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0
107 | TW-BR1110 | TW | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0
108 | TW-BR1120-1 | TW | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-1 | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0
109 | TW-BR1120-2 | TW | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-2 | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0
110 | TW-BR1130-1 | TW | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0
111 | TW-BR1130-2 | TW | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0
112 | TW-BR1140-1 | TW | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0
113 | TW-BR1140-2 | TW | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0
114 | TW-BR1150-1 | TW | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0
115 | TW-BR1150-2 | TW | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0
116 | TW-FW1160 | TW | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0
117 | TW-FW1160(G) | TW | FW1160(G) | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE GAUGE | PD-019 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0
118 | TW-SW1107-A | TW | SW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
119 | TW-SW1107-B | TW | SW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
120 | TW-SW1107-C | TW | SW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
121 | TW-SW1110-A1 | TW | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
122 | TW-SW1110-A1(G) | TW | SW1110-A1(G) | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
123 | TW-SW1110-A2 | TW | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
124 | TW-SW1110-A2(G) | TW | SW1110-A2(G) | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
125 | TW-SW1110-B1 | TW | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
126 | TW-SW1110-B1(G) | TW | SW1110-B1(G) | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
127 | TW-SW1110-B2 | TW | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
128 | TW-SW1110-B2(G) | TW | SW1110-B2(G) | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
129 | TW-SW1503-A | TW | SW1503-A | #1 SEAWATER BOOSTER PUMP A SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
130 | TW-SW1503-B | TW | SW1503-B | #1 SEAWATER BOOSTER PUMP B SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
131 | TW-SW1503-C | TW | SW1503-C | #1 SEAWATER BOOSTER PUMP C SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
132 | TW-SW1551 | TW | SW1551 | #1 SEAWATER PUMP DISCHARGE HEADER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
133 | TW-SW1552 | TW | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
134 | TW-CW1107-A | TW | CW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
135 | TW-CW1107-B | TW | CW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
136 | TW-CW1107-C | TW | CW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
137 | TW-CW1115-A1 | TW | CW1115-A1 | #1 BFP MOTOR P-1115A COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
138 | TW-CW1115-B1 | TW | CW1115-B1 | #1 BFP MOTOR P-1115B COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
139 | TW-CW1151 | TW | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
140 | TW-CW1152 | TW | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
141 | TW-CW1152 | TW | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
142 | TW-CW1153 | TW | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
143 | TW-CW1154-A1 | TW | CW1154-A1 | #1 STEAM TURBINE LUBE OIL COOLER A INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
144 | TW-CW1154-A2 | TW | CW1154-A2 | #1 STEAM TURBINE LUBE OIL COOLER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
145 | TW-CW1154-B1 | TW | CW1154-B1 | #1 STEAM TURBINE LUBE OIL COOLER B INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
146 | TW-CW1154-B2 | TW | CW1154-B2 | #1 STEAM TURBINE LUBE OIL COOLER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
147 | TW-CW1155-A1 | TW | CW1155-A1 | #1 GENERATOR AIR COOLER A-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
148 | TW-CW1155-A2 | TW | CW1155-A2 | #1 GENERATOR AIR COOLER A-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
149 | TW-CW1155-A3 | TW | CW1155-A3 | #1 GENERATOR AIR COOLER A-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
150 | TW-CW1155-A4 | TW | CW1155-A4 | #1 GENERATOR AIR COOLER A-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
151 | TW-CW1155-B1 | TW | CW1155-B1 | #1 GENERATOR AIR COOLER B-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
152 | TW-CW1155-B2 | TW | CW1155-B2 | #1 GENERATOR AIR COOLER B-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
153 | TW-CW1155-B3 | TW | CW1155-B3 | #1 GENERATOR AIR COOLER B-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
154 | TW-CW1155-B4 | TW | CW1155-B4 | #1 GENERATOR AIR COOLER B-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
155 | TW-CW1155-C1 | TW | CW1155-C1 | #1 GENERATOR AIR COOLER C INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
156 | TW-CW1155-C2 | TW | CW1155-C2 | #1 GENERATOR AIR COOLER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
157 | TW-CW1155-D1 | TW | CW1155-D1 | #1 GENERATOR AIR COOLER D INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
158 | TW-CW1155-D2 | TW | CW1155-D2 | #1 GENERATOR AIR COOLER D OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0
159 | TW-DO0003 | TW | DO0003 | DIESEL OIL PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | - | - | - | - | - | FHI | NEW ADDED | 0
160 | TW-DO1006 | TW | DO1006 | #1 DIESEL OIL TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | - | - | - | - | - | FHI | NEW ADDED | 0
161 | TW-PA0151 | TW | PA0151 | PA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-1/6 | 10 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
162 | TW-IA0151 | TW | IA0151 | IA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-2/6 | 10 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0
163 | TW-FG1009-A | TW | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
164 | TW-FG1009-B | TW | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
165 | TW-FG1057-8 | TW | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | PACKAGE (CEMS) | NEW ADDED | 0
166 | TW-FG1090-A | TW | FG1090-A | #1 FURNACE FRONT TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
167 | TW-FG1090-B | TW | FG1090-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
168 | TW-FG1090-C | TW | FG1090-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
169 | TW-FG1090-D | TW | FG1090-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
170 | TW-FG1090-E | TW | FG1090-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
171 | TW-FG1090-F | TW | FG1090-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
172 | TW-FG1090-G | TW | FG1090-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
173 | TW-FG1090-H | TW | FG1090-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
174 | TW-FG1090-I | TW | FG1090-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
175 | TW-FG1091-A | TW | FG1091-A | #1 FURNACE FRONT TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
176 | TW-FG1091-B | TW | FG1091-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
177 | TW-FG1091-C | TW | FG1091-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
178 | TW-FG1091-D | TW | FG1091-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
179 | TW-FG1091-E | TW | FG1091-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
180 | TW-FG1091-F | TW | FG1091-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
181 | TW-FG1091-G | TW | FG1091-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
182 | TW-FG1091-H | TW | FG1091-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
183 | TW-FG1091-I | TW | FG1091-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
184 | TW-FG1092-A | TW | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
185 | TW-FG1092-B | TW | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
186 | TW-FG1095-A | TW | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
187 | TW-FG1095-B | TW | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
188 | TW-FG1096-A | TW | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
189 | TW-FG1096-B | TW | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0
190 | TW-FG1100 | TW | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | - | - | - | FHI | NEW ADDED | 0
191 | TW-FG1101 | TW | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | - | - | - | FHI | NEW ADDED | 0
192 | TW-FG1102 | TW | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | - | - | - | FHI | NEW ADDED | 0
193 | TW-FG1103 | TW | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | - | - | - | FHI | NEW ADDED | 0
194 | TW-FG1104 | TW | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 600 | - | - | - | - | - | FHI | NEW ADDED | 0
195 | TW-FG1105 | TW | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 620 | - | - | - | - | - | FHI | NEW ADDED | 0
196 | TW-FG1106 | TW | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | - | - | - | FHI | NEW ADDED | 0
197 | TW-FG1107 | TW | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 590 | - | - | - | - | - | FHI | NEW ADDED | 0
198 | TW-FG1108 | TW | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 480 | - | - | - | - | - | FHI | NEW ADDED | 0
199 | TW-FG1109 | TW | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | - | - | - | FHI | NEW ADDED | 0
200 | TW-FG1110 | TW | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE ELEMENT-A | PD-051 | ±890mmH2O | 430 | - | - | - | - | - | FHI | NEW ADDED | 0
201 | TW-FG1111 | TW | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 450 | - | - | - | - | - | FHI | NEW ADDED | 0
202 | TW-FG1113 | TW | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE ELEMENT-B | PD-051 | ±890mmH2O | 430 | - | - | - | - | - | FHI | NEW ADDED | 0
203 | TW-FG1124 | TW | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 371 | - | - | - | - | - | FHI | NEW ADDED | 0
204 | TW-FG1125 | TW | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(B) | PD-051 | ±890mmH2O | 371 | - | - | - | - | - | FHI | NEW ADDED | 0
205 | TW-FG1132 | TW | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0
206 | TW-FG1133 | TW | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0
207 | TW-FG1152 | TW | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0
208 | TW-FA1072 | TW | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-052 | 0 | 66 | - | - | - | - | - | FHI | NEW ADDED | 0
209 | TW-FA1073 | TW | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0
210 | TW-FA1074 | TW | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-052 | -340~2500 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0
211 | TW-FA1076 | TW | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0
212 | TW-FA1077 | TW | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-052 | -340~2500 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0
213 | TW-FA1082 | TW | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-053 | 0 | 66 | - | - | - | - | - | FHI | NEW ADDED | 0
214 | TW-FA1083 | TW | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0
215 | TW-FA1084 | TW | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0
216 | TW-FA1086 | TW | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0
217 | TW-FA1087 | TW | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0
218 | TW-FA1055-A | TW | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | - | - | - | FHI | NEW ADDED | 0
219 | TW-FA1055-B | TW | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | - | - | - | FHI | NEW ADDED | 0

## AT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | AT-SP1001 | AT | SP1001 | #1 DEAERATOR UPSTREAM WATER PH | PD-044 | 24 | 65 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
2 | AT-SP1002 | AT | SP1002 | #1 DEAERATOR UPSTREAM WATER CATION CONDUCTIVITY | PD-044 | 24 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
3 | AT-SP1003 | AT | SP1003 | #1 DEAERATOR OUTLET WATER PH | PD-044 | 9 | 180 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
4 | AT-SP1004 | AT | SP1004 | #1 DEAERATOR OUTLET WATER DISSOLVED OXYGEN | PD-044 | 9 | 180 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
5 | AT-SP1005 | AT | SP1005 | #1 DEAERATOR OUTLET WATER CATION CONDUCTIVITY | PD-044 | 9 | 180 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
6 | AT-SP1006 | AT | SP1006 | #1 MAKE-UP WATER PUMP OUTLET WATER PH | PD-044 | 10 | 65 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
7 | AT-SP1007 | AT | SP1007 | #1 MAKE-UP WATER PUMP OUTLET WATER SPECIFIC CONDUCTIVITY | PD-044 | 10 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
8 | AT-SP1008 | AT | SP1008 | #1 MAKE-UP WATER PUMP OUTLET WATER SILICA | PD-044 | 10 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
9 | AT-SP1009 | AT | SP1009 | #1 ECONOMIZER INLET WATER PH | PD-044 | 215 | 275 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
10 | AT-SP1010 | AT | SP1010 | #1 ECONOMIZER INLET WATER DISSOLVED OXYGEN | PD-044 | 215 | 275 | 0~20ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
11 | AT-SP1011 | AT | SP1011 | #1 DRUM WATER(BLOW DOWN) PH | PD-044 | 148 | 343 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
12 | AT-SP1012 | AT | SP1012 | #1 DRUM WATER(BLOW DOWN) SPECIFIC CONDUCTIVITY | PD-044 | 148 | 343 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
13 | AT-SP1013 | AT | SP1013 | #1 DRUM WATER(BLOW DOWN)SILICA | PD-044 | 148 | 343 | 0~500ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
14 | AT-SP1014 | AT | SP1014 | #1 SATURATED STEAM SPECIFIC CONDUCTIVITY | PD-044 | 148 | 343 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
15 | AT-SP1015 | AT | SP1015 | #1 SATURATED STEAM SILICA | PD-044 | 148 | 343 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
16 | AT-SP1016 | AT | SP1016 | #1 MAIN STEAM PH | PD-044 | 144 | 550 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
17 | AT-SP1017 | AT | SP1017 | #1 MAIN STEAM SILICA | PD-044 | 144 | 550 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
18 | AT-SP1018 | AT | SP1018 | #1 CONDENSATE PUMP OUTLET WATER CATION CONDUCTIVITY-1 | PD-044 | 24 | 65.6 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
19 | AT-SP1019 | AT | SP1019 | #1 CONDENSATE PUMP OUTLET WATER CATION CONDUCTIVITY-2 | PD-044 | 24 | 65.6 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
20 | AT-SP1020 | AT | SP1020 | #1 CONDENSATE PUMP OUTLET WATER SODIUM | PD-044 | 24 | 65.6 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
21 | AT-SP1021 | AT | SP1021 | #1 MAIN STEAM LINE CATION CONDUCTIVITY | PD-044 | 144 | 550 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0
22 | AT-FG1057-1 | AT | FG1057-1 | #1 STACK FLUE GAS SOX ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0
23 | AT-FG1057-2 | AT | FG1057-2 | #1 STACK FLUE GAS NOX ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0
24 | AT-FG1057-3 | AT | FG1057-3 | #1 STACK FLUE GAS CO ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0
25 | AT-FG1057-4 | AT | FG1057-4 | #1 STACK FLUE GAS O2 ANALYZER | PD-051 | ±410mmAq | 200 | 0~21% | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0
26 | AT-FG1057-5 | AT | FG1057-5 | #1 STACK FLUE GAS DUST ANALYZER | PD-051 | ±410mmAq | 200 | 0~1000 mg/m3 | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0
27 | AT-FG1057-6 | AT | FG1057-6 | #1 STACK FLUE GAS OPACITY ANALYZER | PD-051 | ±410mmAq | 200 | 0~100% | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0
28 | AT-FG1122 | AT | FG1122 | #1 ECONOMIZER OUTLET FLUE GAS O2 (A) | PD-051 | ±890mmAq | 371 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0
29 | AT-FG1123 | AT | FG1123 | #1 ECONOMIZER OUTLET FLUE GAS O2 (B) | PD-051 | ±890mmAq | 371 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0
30 | AT-FG1131 | AT | FG1131 | #1 AIR PRE-HEATER GAS OUTLET FLUE GAS O2 (C) | PD-051 | ±890mmAq | 200 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0

## CV
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | PCV-MS1001 | PCV | MS1001 | #1 MAIN STEAM BLOW OFF VALVE | PD-011 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
2 | PCV-MS1020 | PCV | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE | PD-011 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
3 | PCV-HR1010 | PCV | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE | PD-012 | 45 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
4 | PCV-AS1010 | PCV | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE | PD-014 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
5 | PCV-AS1020-1 | PCV | AS1020-1 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE (LOW LOAD) | PD-014 | 45 | 395 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
6 | PCV-AS1020-2 | PCV | AS1020-2 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE (HIGH LOAD) | PD-014 | 45 | 395 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
7 | PCV-AS1030 | PCV | AS1030 | #1 DEAERATOR PEGGING STEAM CONTROL VALVE | PD-014 | 13 | 410 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
8 | PCV-SB1053 | PCV | SB1053 | #1 SOOTBLOWING STEAM PRESSURE CONTROL VALVE | PD-015 | 153.5 | 440 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
9 | FCV-CD1120 | FCV | CD1120 | #1 CONDENSATE SYSTEM MINIMUM FLOW RECIRCULATION CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
10 | FCV-CD1121 | FCV | CD1121 | #1 CONDENSATE POLISHIER FLOW CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
11 | LCV-CD1104 | LCV | CD1104 | #1 DEAERATOR LEVEL CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
12 | LCV-CD1110 | LCV | CD1110 | #1 CONDENSATE DUMPING VALVE TO RAW WATER PIT LEVEL CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
13 | LCV-MU1110 | LCV | MU1110 | #1 CONDENER MAKEUP WATER LEVEL CONTROL VALVE | PD-016 | 10 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
14 | TCV-CD1115 | TCV | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
15 | TCV-CD1124 | TCV | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
16 | TCV-CD1126 | TCV | CD1126 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
17 | FCV-FW1130-1 | FCV | FW1130-1 | #1 BOILER FEEDWATER FLOW CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
18 | FCV-FW1130-2 | FCV | FW1130-2 | #1 BOILER FEEDWATER FLOW CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
19 | TCV-FW1060 | TCV | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 100 | 180 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
20 | TCV-FW1110-1 | TCV | FW1110-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
21 | TCV-FW1110-2 | TCV | FW1110-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
22 | TCV-FW1120-1 | TCV | FW1120-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
23 | TCV-FW1120-2 | TCV | FW1120-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
24 | TCV-FW1150 | TCV | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 100 | 180 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
25 | LCV-HD1101-1 | LCV | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
26 | LCV-HD1101-2 | LCV | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
27 | LCV-HD1102-1 | LCV | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
28 | LCV-HD1102-2 | LCV | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
29 | LCV-HD1103-1 | LCV | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 200 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
30 | LCV-HD1103-2 | LCV | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 200 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
31 | LCV-HD1105-1 | LCV | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE | PD-018 | 16 | 210 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
32 | LCV-HD1105-2 | LCV | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE | PD-018 | 16 & Full Vaccum | 210 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
33 | LCV-HD1106-1 | LCV | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE | PD-018 | 45 | 260 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
34 | LCV-HD1106-2 | LCV | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE | PD-018 | 45 & Full Vaccum | 260 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
35 | TCV-CW1201 | TCV | CW1201 | #1 STEAM TURBINE LUBE OIL TEMPERATURE CONTROL VALVE | PD-021 | 10 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
36 | FCV-DO1012 | FCV | DO1012 | #1 DIESEL OIL SUPPLY TO BURNER FLOW CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 1
37 | PCV-DO0002 | PCV | DO0002 | DIESEL OIL SYSTEM PRESSURE CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
38 | PCV-DO1009 | PCV | DO1009 | #1 DIESEL OIL RETURN PRESSURE CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
39 | TCV-FG1116-A | TCV | FG1116-A | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-1 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
40 | TCV-FG1116-B | TCV | FG1116-B | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-2 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
41 | TCV-FG1116-C | TCV | FG1116-C | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-3 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
42 | TCV-FG1116-D | TCV | FG1116-D | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-4 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
43 | TCV-FG1117-A | TCV | FG1117-A | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-1 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
44 | TCV-FG1117-B | TCV | FG1117-B | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-2 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
45 | TCV-FG1117-C | TCV | FG1117-C | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-3 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0
46 | TCV-FG1117-D | TCV | FG1117-D | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-4 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0

## SV
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | SV-CR1011 | SV | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0
2 | SV-CR1012 | SV | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0
3 | SV-MS1011 | SV | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0
4 | SV-MS1020 | SV | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE SOLENOID VALVE (QUICK OPEN) | PD-011 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0
5 | SV-MS1023 | SV | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0
6 | SV-HR1010 | SV | HR1010 | #1 LP TURBINE BYPASS VALVE SOLENOID VALVE(QUICK OPEN) | PD-012 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0
7 | SV-HR1010-1 | SV | HR1010-1 | #1 LP TURBINE BYPASS VALVE WARMING VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0
8 | SV-HR1021 | SV | HR1021 | #1 ILP TURBINE LINEDRAIN POT DP-HR01 DRAIN VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0
9 | SV-HR1022 | SV | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0
10 | SV-SB1054 | SV | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE SOLENOID VALVE | PD-015 | - | - | - | - | - | - | DC24V | FHI |  | 0
11 | SV-SB1059 | SV | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE SOLENOID VALVE | PD-015 | - | - | - | - | - | - | DC24V | FHI |  | 0
12 | SV-CD1004 | SV | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0
13 | SV-CD1005 | SV | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0
14 | SV-CD1006 | SV | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0
15 | SV-CD1104-2 | SV | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0
16 | SV-CD1114 | SV | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0
17 | SV-CD1115 | SV | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE SOLENOID VALVE(QUICK OPEN) | PD-016 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0
18 | SV-CD1123 | SV | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0
19 | SV-CD1125 | SV | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0
20 | SV-FW1060 | SV | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE SOLENOID VALVE(QUICK OPEN) | PD-017 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0
21 | SV-FW1061 | SV | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0
22 | SV-FW1111-1 | SV | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0
23 | SV-FW1111-2 | SV | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0
24 | SV-FW1121-1 | SV | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0
25 | SV-FW1121-2 | SV | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0
26 | SV-FW1151 | SV | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0
27 | SV-MU1109 | SV | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE SOLENOID VALVE | PD-021 | - | - | - | - | - | - | DC24V | FHI |  | 0
28 | SV-IW0113 | SV | IW0113 | TURBINE BUILDING PLUMBING WATER TK INLET SOLENOID VALVE | PD-025 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0
29 | SV-PW0114 | SV | PW0114 | TURBINE BUILDING POTABLE WATER TK INLET SOLENOID VALVE | PD-026 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0
30 | SV-PW0721 | SV | PW0721 | WATER TREATMENT PLANT CONTROL BUILDING POTABLE WATER TANK INLET SOLENOID VALVE | PD-026 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0
31 | SV-FS1005 | SV | FS1005 | #1 FLASH PIPE DRAIN VALVE SOLENOID VALVE | PD-027 | - | - | - | - | - | - | DC24V | FHI |  | 0

## XV
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | XV-CR1011 | XV | CR1011 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 DRAIN VALVE | PD-011 | 45 | 395 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
2 | XV-CR1012 | XV | CR1012 | #1 COLD REHEATER LINE B DRAIN POT DP-CR02 DRAIN VALVE | PD-011 | 45 | 395 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
3 | XV-MS1011 | XV | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE | PD-011 | 144 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
4 | XV-MS1023 | XV | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE | PD-011 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
5 | XV-HR1010-1 | XV | HR1010-1 | #1 LP TURBINE BYPASS VALVE WARMING VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
6 | XV-HR1021 | XV | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
7 | XV-HR1022 | XV | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
8 | XV-SB1054 | XV | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE | PD-015 | 30 | 360 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
9 | XV-SB1059 | XV | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE | PD-015 | 30 | 360 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
10 | XV-CD1004 | XV | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
11 | XV-CD1005 | XV | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
12 | XV-CD1006 | XV | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
13 | XV-CD1104-2 | XV | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER | PD-016 | 8 | 170 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
14 | XV-CD1114 | XV | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
15 | XV-CD1123 | XV | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
16 | XV-CD1125 | XV | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
17 | XV-FW1061 | XV | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 100 | 180 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
18 | XV-FW1111-1 | XV | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
19 | XV-FW1111-2 | XV | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
20 | XV-FW1121-1 | XV | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
21 | XV-FW1121-2 | XV | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
22 | XV-FW1151 | XV | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 100 | 180 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
23 | XV-MU1109 | XV | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE | PD-021 | 10 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0
24 | XV-FS1005 | XV | FS1005 | #1 FLASH PIPE DRAIN VALVE | PD-027 | 8 | 280 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0

## MV
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | MV-AS1394 | MV | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV | PD-011 | 13 | 300 | - | DO | DCS | FIELD | - | FHI |  | 0
2 | MV-MS1391 | MV | MS1391 | #1 MAIN STEAM SHUT-OFF MOV | PD-011 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0
3 | MV-MS1392 | MV | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV | PD-011 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0
4 | MV-HR1391 | MV | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV | PD-012 | 45 | 550 | - | DO | DCS | FIELD | DC TYPE | FHI |  | 0
5 | MV-TS1001 | MV | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV | PD-013 | 45 | 395 | - | DO | DCS | FIELD | - | FHI |  | 0
6 | MV-TS1002 | MV | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0
7 | MV-TS1003 | MV | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD | - | FHI |  | 0
8 | MV-TS1004 | MV | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0
9 | MV-TS1005 | MV | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0
10 | MV-TS1389 | MV | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV(HEATER SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD |  | FHI |  | 0
11 | MV-TS1390 | MV | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV(HEATER SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD |  | FHI |  | 0
12 | MV-TS1391 | MV | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV(TURBINE SIDE) | PD-013 | 45 | 395 | - | DO | DCS | FIELD | - | FHI |  | 0
13 | MV-TS1392 | MV | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV(TURBINE SIDE) | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0
14 | MV-TS1393 | MV | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV(TURBINE SIDE) | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD | - | FHI |  | 0
15 | MV-TS1394 | MV | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV(TURBINE SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0
16 | MV-TS1395 | MV | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV(TURBINE SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0
17 | MV-TS1396 | MV | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV(HEATER SIDE) | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0
18 | MV-TS1397 | MV | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV(HEATER SIDE) | PD-013 | 45 | 395 | - | DO | DCS | FIELD |  | FHI |  | 0
19 | MV-TS1398 | MV | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV(DEAERATORR SIDE) | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD |  | FHI |  | 0
20 | MV-TS1399 | MV | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD |  | FHI |  | 0
21 | MV-TS1400 | MV | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV | PD-013 | 1.5 | 120 | - | DO | DCS | FIELD |  | FHI | NEW ADDED | 0
22 | MV-AS1391 | MV | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV | PD-014 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0
23 | MV-AS1392 | MV | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0
24 | MV-AS1393 | MV | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV | PD-014 | 13 | 300 | - | DO | DCS | FIELD | - | FHI |  | 0
25 | MV-AS1395 | MV | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0
26 | MV-AS1396 | MV | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0
27 | MV-SB1001 | MV | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV | PD-015 | 153.5 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0
28 | MV-CD1001 | MV | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0
29 | MV-CD1002 | MV | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV | PD-016 | 24 | 150 | - | DO | DCS | FIELD | - | FHI |  | 0
30 | MV-CD1003 | MV | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV | PD-016 | 24 | 150 | - | DO | DCS | FIELD | - | FHI |  | 0
31 | MV-CD1007 | MV | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0
32 | MV-CD1008 | MV | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0
33 | MV-MU1001 | MV | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV | PD-016 | 10 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0
34 | MV-FW1001 | MV | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0
35 | MV-FW1002 | MV | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0
36 | MV-FW1391 | MV | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0
37 | MV-FW1392 | MV | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0
38 | MV-BD1001 | MV | BD1001 | #1 BOILER MASS BLOWDOWN MOV | PD-019 | 155.4 | 343 | - | DO | DCS | FIELD | - | FHI |  | 0
39 | MV-BD1002 | MV | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV | PD-019 | 155.4 | 343 | - | DO | DCS | FIELD | - | FHI |  | 0
40 | MV-BR1391 | MV | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV | PD-019 | 153.5 | 440 | - | DO | DCS | FIELD | DC TYPE | FHI |  | 0
41 | MV-SW1001 | MV | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0
42 | MV-SW1002 | MV | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV | PD-020 | 7 | 50 | - | DO | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0
43 | MV-SW1003 | MV | SW1003 | #1 BALL VESSEL T-1116 INLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0
44 | MV-SW1004 | MV | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0
45 | MV-SW1005 | MV | SW1005 | #1 BALL VESSEL T-1115 INLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0
46 | MV-SW1006 | MV | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0
47 | MV-IW0391 | MV | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV | PD-025 | 1.5 | 65 | - | DO | DCS | FIELD |  | FHI | NEW ADDED | 0
48 | MV-AV1391 | MV | AV1391 | #1 CONDENSER VACUUM BREAKER MOV | PD-027 | 1.5 | 120 | - | DO | DCS | FIELD |  | FHI |  | 0

## ZS
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE |  | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  | REMARKS | E
V
1 | ZSC-AS1394 | ZSC | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
2 | ZSO-AS1394 | ZSO | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
3 | TS-AS1394 | TS | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
4 | ZSC-CR1011 | ZSC | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
5 | ZSO-CR1011 | ZSO | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
6 | ZSC-CR1012 | ZSC | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
7 | ZSO-CR1012 | ZSO | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
8 | ZSC-MS1011 | ZSC | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
9 | ZSO-MS1011 | ZSO | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
10 | ZSC-MS1020 | ZSC | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
11 | ZSO-MS1020 | ZSO | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
12 | ZSC-MS1023 | ZSC | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
13 | ZSO-MS1023 | ZSO | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
14 | ZSC-MS1391 | ZSC | MS1391 | #1 MAIN STEAM SHUT-OFF MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
15 | ZSO-MS1391 | ZSO | MS1391 | #1 MAIN STEAM SHUT-OFF MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
16 | TS-MS1391 | TS | MS1391 | #1 MAIN STEAM SHUT-OFF MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
17 | ZSC-MS1392 | ZSC | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
18 | ZSO-MS1392 | ZSO | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
19 | TS-MS1392 | TS | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
20 | ZSC-HR1010 | ZSC | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
21 | ZSO-HR1010 | ZSO | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
22 | ZSC-HR1010-1 | ZSC | HR1010-1 | #1 LP TURBINE BYPASS WARMING VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
23 | ZSO-HR1010-1 | ZSO | HR1010-1 | #1 LP TURBINE BYPASS WARMING VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
24 | ZSC-HR1021 | ZSC | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
25 | ZSO-HR1021 | ZSO | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
26 | ZSC-HR1022 | ZSC | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
27 | ZSO-HR1022 | ZSO | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
28 | ZSC-HR1391 | ZSC | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
29 | ZSO-HR1391 | ZSO | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
30 | TS-HR1391 | TS | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV TORQUE SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
31 | ZSC-TS1001 | ZSC | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
32 | ZSO-TS1001 | ZSO | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
33 | TS-TS1001 | TS | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
34 | ZSC-TS1002 | ZSC | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
35 | ZSO-TS1002 | ZSO | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
36 | TS-TS1002 | TS | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
37 | ZSC-TS1003 | ZSC | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
38 | ZSO-TS1003 | ZSO | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
39 | TS-TS1003 | TS | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
40 | ZSC-TS1004 | ZSC | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
41 | ZSO-TS1004 | ZSO | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
42 | ZSC-TS1004 | ZSC | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV CLOSE POSITION TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
43 | ZSC-TS1005 | ZSC | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
44 | ZSO-TS1005 | ZSO | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
45 | TS-TS1005 | TS | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
46 | ZSC-TS1389 | ZSC | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
47 | ZSO-TS1389 | ZSO | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
48 | TS-TS1389 | TS | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
49 | ZSC-TS1390 | ZSC | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
50 | ZSO-TS1390 | ZSO | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
51 | TS-TS1390 | TS | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
52 | ZSC-TS1391 | ZSC | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
53 | ZSO-TS1391 | ZSO | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
54 | TS-TS1391 | TS | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
55 | ZSC-TS1392 | ZSC | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
56 | ZSO-TS1392 | ZSO | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
57 | TS-TS1392 | TS | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
58 | ZSC-TS1393 | ZSC | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
59 | ZSO-TS1393 | ZSO | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
60 | TS-TS1393 | TS | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
61 | ZSC-TS1394 | ZSC | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
62 | ZSO-TS1394 | ZSO | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
63 | TS-TS1394 | TS | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
64 | ZSC-TS1395 | ZSC | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
65 | ZSO-TS1395 | ZSO | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
66 | TS-TS1395 | TS | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
67 | ZSC-TS1396 | ZSC | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
68 | ZSO-TS1396 | ZSO | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
69 | TS-TS1396 | TS | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
70 | ZSC-TS1397 | ZSC | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
71 | ZSO-TS1397 | ZSO | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
72 | TS-TS1397 | TS | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
73 | ZSC-TS1398 | ZSC | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
74 | ZSO-TS1398 | ZSO | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
75 | TS-TS1398 | TS | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
76 | ZSC-TS1399 | ZSC | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
77 | ZSO-TS1399 | ZSO | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
78 | TS-TS1399 | TS | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
79 | ZSC-TS1400 | ZSC | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0
80 | ZSO-TS1400 | ZSO | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0
81 | TS-TS1400 | TS | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0
82 | ZSC-AS1010 | ZSC | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
83 | ZSO-AS1010 | ZSO | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
84 | ZSC-AS1391 | ZSC | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
85 | ZSO-AS1391 | ZSO | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
86 | TS-AS1391 | TS | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
87 | ZSC-AS1392 | ZSC | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
88 | ZSO-AS1392 | ZSO | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
89 | TS-AS1392 | TS | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
90 | ZSC-AS1393 | ZSC | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
91 | ZSO-AS1393 | ZSO | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
92 | TS-AS1393 | TS | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
93 | ZSC-AS1395 | ZSC | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
94 | ZSO-AS1395 | ZSO | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
95 | TS-AS1395 | TS | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
96 | ZSC-AS1396 | ZSC | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
97 | ZSO-AS1396 | ZSO | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
98 | TS-AS1396 | TS | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
99 | ZSC-SB1001 | ZSC | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
100 | ZSO-SB1001 | ZSO | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
101 | TS-SB1001 | TS | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV TORQUE SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
102 | ZSC-SB1054 | ZSC | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
103 | ZSO-SB1054 | ZSO | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
104 | ZSC-SB1059 | ZSC | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
105 | ZSO-SB1059 | ZSO | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
106 | ZSC-CD1001 | ZSC | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
107 | ZSO-CD1001 | ZSO | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
108 | ZSC-CD1001 | ZSC | CD1001 | #1 LP HEATER NO.1 INLET CONDENSATE SHUT-OFF MOV CLOSE POSITION TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
109 | ZSC-CD1002 | ZSC | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
110 | ZSO-CD1002 | ZSO | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
111 | TS-CD1002 | TS | CD1002 | #1 LP HEATER NO.1 OUTLET CONDESATE SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
112 | ZSC-CD1003 | ZSC | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
113 | ZSO-CD1003 | ZSO | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
114 | TS-CD1003 | TS | CD1003 | #1 LP HEATER NO.1 CONDENSATE BYPASS MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
115 | ZSC-CD1004 | ZSC | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
116 | ZSO-CD1004 | ZSO | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
117 | ZSC-CD1005 | ZSC | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
118 | ZSO-CD1005 | ZSO | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
119 | ZSC-CD1006 | ZSC | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
120 | ZSO-CD1006 | ZSO | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
121 | ZSC-CD1007 | ZSC | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
122 | ZSO-CD1007 | ZSO | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
123 | TS-CD1007 | TS | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
124 | ZSC-CD1008 | ZSC | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
125 | ZSO-CD1008 | ZSO | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
126 | TS-CD1008 | TS | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
127 | ZSC-CD1104-2 | ZSC | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
128 | ZSO-CD1104-2 | ZSO | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
129 | ZSC-CD1115 | ZSC | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
130 | ZSO-CD1115 | ZSO | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
131 | ZSC-CD1123 | ZSC | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
132 | ZSO-CD1123 | ZSO | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
133 | ZSC-CD1124 | ZSC | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
134 | ZSO-CD1124 | ZSO | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
135 | ZSC-CD1125 | ZSC | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
136 | ZSO-CD1125 | ZSO | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
137 | ZSC-CD1126 | ZSC | CD1126 | #1 GLAND STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
138 | ZSO-CD1126 | ZSO | CD1126 | #1 GLAND STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
139 | ZSC-MU1001 | ZSC | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
140 | ZSO-MU1001 | ZSO | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
141 | TS-MU1001 | TS | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
142 | ZSC-CD1114 | ZSC | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
143 | ZSO-CD1114 | ZSO | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
144 | ZSC-FW1001 | ZSC | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
145 | ZSO-FW1001 | ZSO | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
146 | TS-FW1001 | TS | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
147 | ZSC-FW1002 | ZSC | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
148 | ZSO-FW1002 | ZSO | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
149 | TS-FW1002 | TS | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
150 | ZSO-FW1031 | ZSO | FW1031 | #1 BFP(A) SUCTION MANUAL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
151 | ZSO-FW1032 | ZSO | FW1032 | #1 BFP(B) SUCTION MANUAL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
152 | ZSC-FW1060 | ZSC | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
153 | ZSO-FW1060 | ZSO | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
154 | ZSC-FW1061 | ZSC | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
155 | ZSO-FW1061 | ZSO | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
156 | ZSC-FW1111-1 | ZSC | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
157 | ZSO-FW1111-1 | ZSO | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
158 | ZSC-FW1111-2 | ZSC | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
159 | ZSO-FW1111-2 | ZSO | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
160 | ZSC-FW1121-1 | ZSC | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
161 | ZSO-FW1121-1 | ZSO | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
162 | ZSC-FW1121-2 | ZSC | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUPCLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
163 | ZSO-FW1121-2 | ZSO | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUPOPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
164 | ZSC-FW1150 | ZSC | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
165 | ZSO-FW1150 | ZSO | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
166 | ZSC-FW1151 | ZSC | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
167 | ZSO-FW1151 | ZSO | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
168 | ZSC-FW1391 | ZSC | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
169 | ZSO-FW1391 | ZSO | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
170 | TS-FW1391 | TS | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
171 | ZSC-FW1392 | ZSC | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
172 | ZSO-FW1392 | ZSO | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
173 | TS-FW1392 | TS | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
174 | ZSC-BD1001 | ZSC | BD1001 | #1 BOILER MASS BLOWDOWN MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
175 | ZSO-BD1001 | ZSO | BD1001 | #1 BOILER MASS BLOWDOWN MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
176 | TS-BD1001 | TS | BD1001 | #1 BOILER MASS BLOWDOWN MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
177 | ZSC-BD1002 | ZSC | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
178 | ZSO-BD1002 | ZSO | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
179 | TS-BD1002 | TS | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
180 | ZSC-BR1391 | ZSC | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
181 | ZSO-BR1391 | ZSO | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
182 | TS-BR1391 | TS | BR1391 | #1 SUPERHEATER PANEL NO.1 INLET TO REHEATER MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
183 | ZSC-SW1001 | ZSC | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0
184 | ZSO-SW1001 | ZSO | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0
185 | TS-SW1001 | TS | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0
186 | ZSC-SW1002 | ZSC | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0
187 | ZSO-SW1002 | ZSO | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0
188 | TS-SW1002 | TS | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0
189 | ZSC-SW1003 | ZSC | SW1003 | #1 BALL VESSEL T-1116 INLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
190 | ZSO-SW1003 | ZSO | SW1003 | #1 BALL VESSEL T-1116 INLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
191 | TS-SW1003 | TS | SW1003 | #1 BALL VESSEL T-1116 INLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
192 | ZSC-SW1004 | ZSC | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
193 | ZSO-SW1004 | ZSO | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
194 | TS-SW1004 | TS | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
195 | ZSC-SW1005 | ZSC | SW1005 | #1 BALL VESSEL T-1115 INLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
196 | ZSO-SW1005 | ZSO | SW1005 | #1 BALL VESSEL T-1115 INLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
197 | TS-SW1005 | TS | SW1005 | #1 BALL VESSEL T-1115 INLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
198 | ZSC-SW1006 | ZSC | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
199 | ZSO-SW1006 | ZSO | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
200 | TS-SW1006 | TS | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0
201 | ZSO-MU1109 | ZSO | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE OPEN POSITION SWITCH | PD-021 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
202 | ZSC-MU1109 | ZSC | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE CLOSE POSITION SWITCH | PD-021 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
203 | ZSC-IW0391 | ZSC | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV CLOSE POSITION SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
204 | ZSO-IW0391 | ZSO | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV OPEN POSITION SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
205 | TS-IW0391 | TS | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV TORQUE SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
206 | ZSC-AV1391 | ZSC | AV1391 | #1 CONDENSER VACUUM BREAKER MOV CLOSE POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
207 | ZSO-AV1391 | ZSO | AV1391 | #1 CONDENSER VACUUM BREAKER MOV OPEN POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
208 | TS-AV1391 | TS | AV1391 | #1 CONDENSER VACUUM BREAKER MOV TORQUE SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
209 | ZSC-FS1005 | ZSC | FS1005 | #1 FLASH PIPE DRAIN VALVE CLOSE POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
210 | ZSO-FS1005 | ZSO | FS1005 | #1 FLASH PIPE DRAIN VALVE OPEN POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0

## ZT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | ZT-AS1394 | ZT | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
2 | ZT-MS1001 | ZT | MS1001 | #1 MAIN STEAM BLOW OFF VALVE POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
3 | ZT-MS1020 | ZT | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
4 | ZT-MS1391 | ZT | MS1391 | #1 MAIN STEAM SHUT-OFF MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
5 | ZT-MS1392 | ZT | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
6 | ZT-HR1010 | ZT | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE POSITION TRANSMITTER | PD-012 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
7 | ZT-HR1391 | ZT | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV POSITION TRANSMITTER | PD-012 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
8 | ZT-TS1001 | ZT | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
9 | ZT-TS1002 | ZT | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
10 | ZT-TS1003 | ZT | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
11 | ZT-TS1004 | ZT | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
12 | ZT-TS1005 | ZT | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
13 | ZT-TS1389 | ZT | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
14 | ZT-TS1390 | ZT | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
15 | ZT-TS1391 | ZT | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
16 | ZT-TS1392 | ZT | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
17 | ZT-TS1393 | ZT | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
18 | ZT-TS1394 | ZT | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
19 | ZT-TS1395 | ZT | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
20 | ZT-TS1396 | ZT | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
21 | ZT-TS1397 | ZT | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
22 | ZT-TS1398 | ZT | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER(DEAERATORR SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
23 | ZT-TS1399 | ZT | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
24 | ZT-TS1400 | ZT | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI | NEW ADDED | 0
25 | ZT-AS1010 | ZT | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
26 | ZT-AS1020-1 | ZT | AS1020-1 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER (LOW LOAD) | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
27 | ZT-AS1020-2 | ZT | AS1020-2 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER (HIGH LOAD) | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
28 | ZT-AS1030 | ZT | AS1030 | #1 DEAERATOR PEGGING STEAM CONTROL VALVE POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
29 | ZT-AS1391 | ZT | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
30 | ZT-AS1392 | ZT | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
31 | ZT-AS1393 | ZT | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
32 | ZT-AS1395 | ZT | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
33 | ZT-AS1396 | ZT | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
34 | ZT-SB1001 | ZT | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV POSITION TRANSMITTER | PD-015 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
35 | ZT-SB1053 | ZT | SB1053 | #1 SOOT BLOWING STEAM PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-015 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
36 | ZT-CD1001 | ZT | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
37 | ZT-CD1002 | ZT | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
38 | ZT-CD1003 | ZT | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
39 | ZT-CD1007 | ZT | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
40 | ZT-CD1008 | ZT | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
41 | ZT-CD1104 | ZT | CD1104 | #1 DEAERATOR LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
42 | ZT-CD1110 | ZT | CD1110 | #1 CONDENSATE DUMPING VALVE TO RAW WATER PIT LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
43 | ZT-CD1115 | ZT | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
44 | ZT-CD1120 | ZT | CD1120 | #1 CONDENSATE SYSTEM MINIMUM FLOW RECIRCULATION CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
45 | ZT-CD1121 | ZT | CD1121 | #1 CONDENSATE POLISHIER FLOW CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
46 | ZT-CD1124 | ZT | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
47 | ZT-CD1126 | ZT | CD1126 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
48 | ZT-MU1001 | ZT | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
49 | ZT-MU1110 | ZT | MU1110 | #1 CONDENER MAKEUP WATER LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
50 | ZT-FW1001 | ZT | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
51 | ZT-FW1002 | ZT | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
52 | ZT-FW1060 | ZT | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
53 | ZT-FW1110-1 | ZT | FW1110-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
54 | ZT-FW1110-2 | ZT | FW1110-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
55 | ZT-FW1120-1 | ZT | FW1120-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
56 | ZT-FW1120-2 | ZT | FW1120-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
57 | ZT-FW1130-1 | ZT | FW1130-1 | #1 BOILER FEEDWATER FLOW CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
58 | ZT-FW1130-2 | ZT | FW1130-2 | #1 BOILER FEEDWATER FLOW CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
59 | ZT-FW1150 | ZT | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
60 | ZT-FW1391 | ZT | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
61 | ZT-FW1392 | ZT | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
62 | ZT-HD1101-1 | ZT | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
63 | ZT-HD1101-2 | ZT | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
64 | ZT-HD1102-1 | ZT | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
65 | ZT-HD1102-2 | ZT | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
66 | ZT-HD1103-1 | ZT | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
67 | ZT-HD1103-2 | ZT | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
68 | ZT-HD1105-1 | ZT | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
69 | ZT-HD1105-2 | ZT | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
70 | ZT-HD1106-1 | ZT | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
71 | ZT-HD1106-2 | ZT | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
72 | ZT-BD1001 | ZT | BD1001 | #1 BOILER MASS BLOWDOWN MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
73 | ZT-BD1002 | ZT | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
74 | ZT-BR1391 | ZT | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
75 | ZT-CW1201 | ZT | CW1201 | #1 STEAM TURBINE LUBE OIL TEMPERATURE CONTROL VALVE POSITION TRANSMITTER | PD-021 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
76 | ZT-DO0002 | ZT | DO0002 | DIESEL OIL SYSTEM PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
77 | ZT-DO1009 | ZT | DO1009 | #1 DIESEL OIL RETURN PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
78 | ZT-DO1012 | ZT | DO1012 | #1 DIESEL OIL SUPPLY TO BURNER #1 FLOW CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
79 | ZT-IW0391 | ZT | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV POSITION TRANSMITTER | PD-025 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
80 | ZT-AV1391 | ZT | AV1391 | #1 CONDENSER VACUUM BREAKER MOV POSITION TRANSMITTER | PD-027 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
81 | ZT-FG1116-A | ZT | FG1116-A | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-1 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
82 | ZT-FG1116-B | ZT | FG1116-B | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-2 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
83 | ZT-FG1116-C | ZT | FG1116-C | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-3 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
84 | ZT-FG1116-D | ZT | FG1116-D | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-4 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
85 | ZT-FG1117-A | ZT | FG1117-A | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-1 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
86 | ZT-FG1117-B | ZT | FG1117-B | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-2 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
87 | ZT-FG1117-C | ZT | FG1117-C | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-3 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
88 | ZT-FG1117-D | ZT | FG1117-D | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-4 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0

## VT
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | VT-CD1116-A1 | VT | CD1116-A1 | #1 CONDENSATE PUMP (A) VIBRATION TRANSMITTER-1 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0
2 | VT-CD1116-A2 | VT | CD1116-A2 | #1 CONDENSATE PUMP (A) VIBRATION TRANSMITTER-2 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0
3 | VT-CD1116-A3 | VT | CD1116-A3 | #1 CONDENSATE PUMP (A) MOTOR DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0
4 | VT-CD1116-A4 | VT | CD1116-A4 | #1 CONDENSATE PUMP (A) MOTOR NON-DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0
5 | VT-CD1116-B1 | VT | CD1116-B1 | #1 CONDENSATE PUMP (B) VIBRATION TRANSMITTER-1 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0
6 | VT-CD1116-B2 | VT | CD1116-B2 | #1 CONDENSATE PUMP (B) VIBRATION TRANSMITTER-2 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0
7 | VT-CD1116-B3 | VT | CD1116-B3 | #1 CONDENSATE PUMP (B) MOTOR DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0
8 | VT-CD1116-B4 | VT | CD1116-B4 | #1 CONDENSATE PUMP (B) MOTOR NON-DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0
9 | VT-FW1115-A11 | VT | FW1115-A11 | #1 BFP(A) PUMP CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
10 | VT-FW1115-A12 | VT | FW1115-A12 | #1 BFP(A) PUMP CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
11 | VT-FW1115-A21 | VT | FW1115-A21 | #1 BFP(A) PUMP CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
12 | VT-FW1115-A22 | VT | FW1115-A22 | #1 BFP(A) PUMP CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
13 | VT-FW1115-A31 | VT | FW1115-A31 | #1 BFP(A) MOTOR CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
14 | VT-FW1115-A32 | VT | FW1115-A32 | #1 BFP(A) MOTOR CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
15 | VT-FW1115-A41 | VT | FW1115-A41 | #1 BFP(A) MOTOR CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
16 | VT-FW1115-A42 | VT | FW1115-A42 | #1 BFP(A) MOTOR CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
17 | VT-FW1115-B11 | VT | FW1115-B11 | #1 BFP(B) PUMP CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
18 | VT-FW1115-B12 | VT | FW1115-B12 | #1 BFP(B) PUMP CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
19 | VT-FW1115-B21 | VT | FW1115-B21 | #1 BFP(B) PUMP CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
20 | VT-FW1115-B22 | VT | FW1115-B22 | #1 BFP(B) PUMP CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
21 | VT-FW1115-B31 | VT | FW1115-B31 | #1 BFP(B) MOTOR CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
22 | VT-FW1115-B32 | VT | FW1115-B32 | #1 BFP(B) MOTOR CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
23 | VT-FW1115-B41 | VT | FW1115-B41 | #1 BFP(B) MOTOR CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
24 | VT-FW1115-B42 | VT | FW1115-B42 | #1 BFP(B) MOTOR CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0
25 | VT-SW1501-A1 | VT | SW1501-A1 | #1 SEWATER PUMP (A) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0
26 | VT-SW1501-A2 | VT | SW1501-A2 | #1 SEWATER PUMP (A) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0
27 | VT-SW1501-B1 | VT | SW1501-B1 | #1 SEWATER PUMP (B) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0
28 | VT-SW1501-B2 | VT | SW1501-B2 | #1 SEWATER PUMP (B) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0
29 | VT-SW1501-C1 | VT | SW1501-C1 | #1 SEWATER PUMP (C) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0
30 | VT-SW1501-C2 | VT | SW1501-C2 | #1 SEWATER PUMP (C) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0
31 | VT-CW1108-A3 | VT | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0
32 | VT-CW1108-A4 | VT | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0
33 | VT-CW1108-B3 | VT | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0
34 | VT-CW1108-B4 | VT | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0

## AIR CANNON
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
AIR CANNON SYSTEM
1 | PG-PA1066A~I | PG | PA1066A~I | #1 COAL BUNKER A (T-1008A) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1
2 | PG-PA1067A~I | PG | PA1067A~I | #1 COAL BUNKER B (T-1008B) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1
3 | PG-PA1068A~I | PG | PA1068A~I | #1 COAL BUNKER C (T-1008C) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1
4 | SV-PA1066A~I | SV | PA1066A~I | #1 COAL BUNKER A (T-1008A) AIR CANNON SOLENOID VALVE SV-PA1066A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1
5 | SV-PA1067A~I | SV | PA1067A~I | #1 COAL BUNKER B (T-1008B) AIR CANNON SOLENOID VALVE SV-PA1067A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1
6 | SV-PA1068A~I | SV | PA1068A~I | #1 COAL BUNKER C (T-1008C) AIR CANNON SOLENOID VALVE SV-PA1068A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1

## AIR PRE-HEATER
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
1 | LG-FA1052-1 | LG | FA1052-1 | #1 AIR PRE-HEATER LEVEL GLASS BOTTOM BERATING | - | - | - | - | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 0
2 | LG-FA1052-2 | LG | FA1052-2 | #1 AIR PRE-HEATER LEVEL GLASS TOP BERATING | - | - | - | - | - | - |  | - | PACKAGE (AIR PRE HEATER) |  | 1
3 | PG-PA1052 | PG | PA1052 | #1 AIR PRE-HEATER AIR MOTOR SUPPLY PRESSURE GAUGE | - | - | - | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (AIR PRE HEATER) | NEW ADDED | 1
4 | PT-SB1040 | PT | SB1040 | #1 HOT END SOOTBLOWER STEAM PRESSURE TRANSMITTER | - | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0
5 | PT-SB1042 | PT | SB1042 | #1 COLD END SOOTBLOWER STEAM PRESSURE TRANSMITTER | - | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0
6 | SE-FA1052-1 | SE | FA1052-1 | #1 AIR PRE-HEATER ROTOR SPEED SENSOR-1 | - | - | - | 0-12 mm | AI | FIELD | SM-1 | - | PACKAGE (AIR PRE HEATER) |  | 0
7 | SE-FA1052-2 | SE | FA1052-2 | #1 AIR PRE-HEATER ROTOR SPEED SENSOR-2 | - | - | - | 0-12 mm | AI | FIELD | SM-2 | - | PACKAGE (AIR PRE HEATER) |  | 0
8 | ST-FA1502-1 | ST | FA1502-1 | #1 AIR PRE-HEATER ROTOR SPEED MONITOR-1 | - | - | - | 0-20000 | AI | LCP | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0
9 | ST-FA1502-2 | ST | FA1502-2 | #1 AIR PRE-HEATER ROTOR SPEED MONITOR-2 | - | - | - | 0-20000 | AI | LCP | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0
10 | SV-FA1052-1 | SV | FA1052-1 | #1 AIR PRE-HEATER SOLENOID FOR AIR MOTOR | - | - | 0-10 BarG | - | DO | DCS | LOCAL INVERTER PANEL | 24VDC | PACKAGE (AIR PRE HEATER) |  | 1
11 | TE-FA1052-1 | TE | FA1052-1 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-1 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0
12 | TE-FA1052-2 | TE | FA1052-2 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-2 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0
13 | TE-FA1052-3 | TE | FA1052-3 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-3 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0
14 | TE-FA1052-4 | TE | FA1052-4 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-4 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0
15 | TE-FA1052-5 | TE | FA1052-5 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-5 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0
16 | TE-FA1052-6 | TE | FA1052-6 | #1 AIR PRE-HEATER TOP BEARING TEMPERATUTRE | - | - | - | -200~850℃ | AI | FIELD | TT | RTD | PACKAGE (AIR PRE HEATER) |  | 0
17 | TE-FA1052-7 | TE | FA1052-7 | #1 AIR PRE-HEATER BOOTOM BEARING TEMPERATUTRE | - | - | - | -200~850℃ | AI | FIELD | TT | RTD | PACKAGE (AIR PRE HEATER) |  | 0
18 | TT-FA1052-6 | TT | FA1052-6 | #1 AIR PRE-HEATER TOP BEARING TEMPERATUTRE TRANSMITTER | - | - | - | 0~150℃ | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0
19 | TT-FA1052-7 | TT | FA1052-7 | #1 AIR PRE-HEATER BOOTOM BEARING TEMPERATUTRE TRANSMITTER | - | - | - | 0~150℃ | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0
20 | ZSF-SB1040 | ZSF | SB1040 | #1 HOT END SOOTBLOWER LANCE EXTEND LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1
21 | ZSF-SB1042 | ZSF | SB1042 | #1 COLD END SOOTBLOWER LANCE EXTEND LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1
22 | ZSR-SB1040 | ZSR | SB1040 | #1 HOT END SOOTBLOWER LANCE PARK LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1
23 | ZSR-SB1042 | ZSR | SB1042 | #1 COLD END SOOTBLOWER LANCE PARK LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1
24 | DPG-FG1052-1 | DPG | FG1052-1 | #1 SECONDARY AIR/GAS HOT END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1
25 | DPG-FG1052-2 | DPG | FG1052-2 | #1 PRIMARY AIR/GAS HOT END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1
26 | DPG-FG1052-3 | DPG | FG1052-3 | #1 SECONDARY AIR/GAS COLD END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1
27 | DPG-FG1052-4 | DPG | FG1052-4 | #1 PRIMARY AIR/GAS COLD END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1

## BOTTOM ASH COOLER
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
BOTTOM ASH COOLER SYSTEM
1 | TE-CW1156 | TE | CW1156 | #1 AUXILIARY COOLING WATER TEMPERATURE ELEMENT AT ASH CONVEYOR COMMON HEADER | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (COOLING SCREW) |  | 0
2 | TT-CW1156 | TT | CW1156 | #1 AUXILIARY COOLING WATER TEMPERATURE AT BOTTOM ASH SCREW CONVEYOR COMMON HEADER | PD-021 | - | - | 0~150℃ | AI 4~20mA | FIELD | DCS | SMART | PACKAGE (COOLING SCREW) |  | 0
3 | FS-CW1060-A1 | FS | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
4 | FS-CW1060-A2 | FS | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
5 | FS-CW1060-B1 | FS | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
6 | FS-CW1060-B2 | FS | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
7 | FS-CW1060-C1 | FS | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
8 | FS-CW1060-C2 | FS | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
9 | FS-CW1060-D1 | FS | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
10 | FS-CW1060-D2 | FS | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
11 | PG-CW1060-A | PG | CW1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
12 | PG-CW1060-A1 | PG | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
13 | PG-CW1060-A2 | PG | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
14 | PG-CW1060-B | PG | CW1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
15 | PG-CW1060-B1 | PG | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
16 | PG-CW1060-B2 | PG | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
17 | PG-CW1060-C | PG | CW1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
18 | PG-CW1060-C1 | PG | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
19 | PG-CW1060-C2 | PG | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
20 | PG-CW1060-D | PG | CW1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
21 | PG-CW1060-D1 | PG | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
22 | PG-CW1060-D2 | PG | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
23 | PG-PA1060-A | PG | PA1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
24 | PG-PA1060-B | PG | PA1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
25 | PG-PA1060-C | PG | PA1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
26 | PG-PA1060-C | PG | PA1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060D PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
27 | PT-CW1156 | PT | CW1156 | #1 AUXILIARY COOLING WATER PRESSURE TRANSMITTER AT BOTTOM ASH SCREW CONVEYOR COMMON HEADER | PD-072 | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
28 | SS-BH1060-A | SS | BH1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0
29 | SS-BH1060-B | SS | BH1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0
30 | SS-BH1060-C | SS | BH1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0
31 | SS-BH1060-D | SS | BH1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0
32 | TE-BH1060-A1 | TE | BH1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
33 | TE-BH1060-A2 | TE | BH1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
34 | TE-BH1060-B1 | TE | BH1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
35 | TE-BH1060-B2 | TE | BH1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
36 | TE-BH1060-C1 | TE | BH1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
37 | TE-BH1060-C2 | TE | BH1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
38 | TE-BH1060-D1 | TE | BH1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
39 | TE-BH1060-D2 | TE | BH1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
40 | TE-CW1060-A1 | TE | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
41 | TE-CW1060-A2 | TE | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
42 | TE-CW1060-B1 | TE | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
43 | TE-CW1060-B2 | TE | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
44 | TE-CW1060-C1 | TE | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
45 | TE-CW1060-C2 | TE | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
46 | TE-CW1060-D1 | TE | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
47 | TE-CW1060-D2 | TE | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0
48 | TG-CW1060-A | TG | CW1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
49 | TG-CW1060-A1 | TG | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
50 | TG-CW1060-A2 | TG | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
51 | TG-CW1060-B | TG | CW1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
52 | TG-CW1060-B1 | TG | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
53 | TG-CW1060-B2 | TG | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
54 | TG-CW1060-C | TG | CW1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
55 | TG-CW1060-C1 | TG | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
56 | TG-CW1060-C2 | TG | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
57 | TG-CW1060-D | TG | CW1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
58 | TG-CW1060-D1 | TG | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
59 | TG-CW1060-D2 | TG | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0
60 | TT-BH1060-A1 | TT | BH1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
61 | TT-BH1060-A2 | TT | BH1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
62 | TT-BH1060-B1 | TT | BH1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
63 | TT-BH1060-B2 | TT | BH1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
64 | TT-BH1060-C1 | TT | BH1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
65 | TT-BH1060-C2 | TT | BH1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
66 | TT-BH1060-D1 | TT | BH1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
67 | TT-BH1060-D2 | TT | BH1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0
68 | TT-CW1060-A1 | TT | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
69 | TT-CW1060-A2 | TT | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
70 | TT-CW1060-B1 | TT | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
71 | TT-CW1060-B2 | TT | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
72 | TT-CW1060-C1 | TT | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
73 | TT-CW1060-C2 | TT | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
74 | TT-CW1060-D1 | TT | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0
75 | TT-CW1060-D2 | TT | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0

## COAL FEEDER
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
COAL FEEDER SYSTEM
7 | PS-IA1061-D1 | PS | IA1061-D1 | #1 COAL FEEDER D INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-052 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | DELETED 20150529 | 1
8 | PS-IA1061-D2 | PS | IA1061-D2 | #1 COAL FEEDER D INSTRUMENT AIR PRESSURE SWITCH LOW | PD-052 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | DELETED 20150529 | 1
1 | FT-CL1061-A | FT | CL1061-A | #1 A-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
2 | FT-CL1061-B | FT | CL1061-B | #1 B-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
3 | FT-CL1061-C | FT | CL1061-C | #1 C-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
4 | LS-CL1061-A3 | LS | CL1061-A3 | #1 A-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
5 | LS-CL1061-A4 | LS | CL1061-A4 | #1 A-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
6 | LS-CL1061-A5 | LS | CL1061-A5 | #1 A-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
7 | LS-CL1061-A6 | LS | CL1061-A6 | #1 A-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
8 | LS-CL1061-B3 | LS | CL1061-B3 | #1 B-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
9 | LS-CL1061-B4 | LS | CL1061-B4 | #1 B-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
10 | LS-CL1061-B5 | LS | CL1061-B5 | #1 B-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
11 | LS-CL1061-B6 | LS | CL1061-B6 | #1 B-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
12 | LS-CL1061-C3 | LS | CL1061-C3 | #1 C-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
13 | LS-CL1061-C4 | LS | CL1061-C4 | #1 C-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
14 | LS-CL1061-C5 | LS | CL1061-C5 | #1 C-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
15 | LS-CL1061-C6 | LS | CL1061-C6 | #1 C-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
16 | PS-IA1061-A1 | PS | IA1061-A1 | #1 COAL FEEDER A INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1
17 | PS-IA1061-A1 | PS | IA1061-A1 | #1 A-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
18 | PS-IA1061-A2 | PS | IA1061-A2 | #1 COAL FEEDER A INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1
19 | PS-IA1061-A2 | PS | IA1061-A2 | #1 A-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
20 | PS-IA1061-B1 | PS | IA1061-B1 | #1 COAL FEEDER B INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1
21 | PS-IA1061-B1 | PS | IA1061-B1 | #1 B-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
22 | PS-IA1061-B2 | PS | IA1061-B2 | #1 COAL FEEDER B INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1
23 | PS-IA1061-B2 | PS | IA1061-B2 | #1 B-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
24 | PS-IA1061-C1 | PS | IA1061-C1 | #1 COAL FEEDER C INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1
25 | PS-IA1061-C1 | PS | IA1061-C1 | #1 C-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
26 | PS-IA1061-C2 | PS | IA1061-C2 | #1 COAL FEEDER C INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1
27 | PS-IA1061-C2 | PS | IA1061-C2 | #1 C-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
28 | SE-CL1061-A | SE | CL1061-A | #1 A-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
29 | SE-CL1061-B | SE | CL1061-B | #1 B-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
30 | SE-CL1061-C | SE | CL1061-C | #1 C-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
31 | SV-CL1061-A7 | SV | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
32 | SV-CL1061-B7 | SV | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
33 | SV-CL1061-C7 | SV | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
34 | TS-CL1061-A | TS | CL1061-A | #1 A-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
35 | TS-CL1061-B | TS | CL1061-B | #1 B-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
36 | TS-CL1061-C | TS | CL1061-C | #1 C-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
37 | WT-CL1061-A1 | WT | CL1061-A1 | #1 A-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
38 | WT-CL1061-A2 | WT | CL1061-A2 | #1 A-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
39 | WT-CL1061-B1 | WT | CL1061-B1 | #1 B-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
40 | WT-CL1061-B2 | WT | CL1061-B2 | #1 B-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
41 | WT-CL1061-C1 | WT | CL1061-C1 | #1 C-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
42 | WT-CL1061-C2 | WT | CL1061-C2 | #1 C-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
43 | XV-CL1061-A7 | XV | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
44 | XV-CL1061-B7 | XV | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
45 | XV-CL1061-C7 | XV | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
46 | ZSC-CL1061-A1 | ZSC | CL1061-A1 | #1 A-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
47 | ZSC-CL1061-A2 | ZSC | CL1061-A2 | #1 A-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
48 | ZSC-CL1061-A7 | ZSC | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
49 | ZSC-CL1061-B1 | ZSC | CL1061-B1 | #1 B-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
50 | ZSC-CL1061-B2 | ZSC | CL1061-B2 | #1 B-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
51 | ZSC-CL1061-B7 | ZSC | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
52 | ZSC-CL1061-C1 | ZSC | CL1061-C1 | #1 C-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
53 | ZSC-CL1061-C2 | ZSC | CL1061-C2 | #1 C-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
54 | ZSC-CL1061-C7 | ZSC | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
55 | ZSO-CL1061-A1 | ZSO | CL1061-A1 | #1 A-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
56 | ZSO-CL1061-A2 | ZSO | CL1061-A2 | #1 A-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
57 | ZSO-CL1061-A7 | ZSO | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
58 | ZSO-CL1061-B1 | ZSO | CL1061-B1 | #1 B-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
59 | ZSO-CL1061-B2 | ZSO | CL1061-B2 | #1 B-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
60 | ZSO-CL1061-B7 | ZSO | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
61 | ZSO-CL1061-C1 | ZSO | CL1061-C1 | #1 C-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
62 | ZSO-CL1061-C2 | ZSO | CL1061-C2 | #1 C-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1
63 | ZSO-CL1061-C7 | ZSO | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1

## DIESEL OIL AND BURNER
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
DIESEL OIL AND BURNER SYSTEM
1 | BT-DO1043-A | BT | DO1043-A | #1 BURNER(A) COMPACT FLAME DETECTOR | PD-022,2/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0
2 | FCV-DO1043-A3 | FCV | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE | PD-022,2/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0
3 | FE-DO1043-A | FE | DO1043-A | #1 BURNER(A) DIESEL OIL FLOW ELEMENT | PD-022,2/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1
4 | FT-DO1043-A | FT | DO1043-A | #1 BURNER(A) DIESEL OIL FLOW TRANSMITTER | PD-022,2/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
5 | MCV-FA1043-A | MCV | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,2/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1
6 | PG-DO1043-A | PG | DO1043-A | #1 BURNER(A) DIESEL OIL PRESSURE GAUGE | PD-022,2/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
7 | PG-DO1043-A2 | PG | DO1043-A2 | #1 BURNER(A) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,2/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
8 | PG-FA1043-A | PG | FA1043-A | #1 BURNER(A) AIR PRESSURE GAUGE | PD-022,2/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
9 | PG-PA1043-A1 | PG | PA1043-A1 | #1 BURNER(A) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,2/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
10 | PG-PA1043-A2 | PG | PA1043-A2 | #1 BURNER(A) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,2/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
11 | PRV-PA1043-A | PRV | PA1043-A | #1 BURNER(A) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,2/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1
12 | PRV-PA1043-A1 | PRV | PA1043-A1 | #1 BURNER(A) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,2/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
13 | PSH-DO1043-A1 | PSH | DO1043-A1 | #1 BURNER(A) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,2/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
14 | PSL-PA1043-A1 | PSL | PA1043-A1 | #1 BURNER(A) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,2/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
15 | PT-DO1043-A2 | PT | DO1043-A2 | #1 BURNER(A) DIESEL OIL PRESSURE TRANSMITTER | PD-022,2/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
16 | SV-DO1043-A1 | SV | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
17 | SV-DO1043-A2 | SV | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
18 | SV-PA1043-A2 | SV | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
19 | SV-PA1043-A3 | SV | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
20 | SVE-DO1043-A4 | SVE | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 EXTENDING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
21 | SVE-DO1043-A5 | SVE | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
22 | SVR-DO1043-A5 | SVR | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
23 | TS-FA1043-A | TS | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
24 | XV-DO1043-A1 | XV | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
25 | XV-DO1043-A2 | XV | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
26 | XV-PA1043-A2 | XV | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
27 | XV-PA1043-A3 | XV | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
28 | ZS-DO1043-A3 | ZS | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
29 | ZS1-FA1043-A | ZS1 | FA1043-A | #1 BURNER(A) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
30 | ZS2-FA1043-A | ZS2 | FA1043-A | #1 BURNER(A) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
31 | ZSC-DO1043-A1 | ZSC | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
32 | ZSC-DO1043-A2 | ZSC | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
33 | ZSC-FA1043-A | ZSC | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
34 | ZSC-PA1043-A2 | ZSC | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
35 | ZSC-PA1043-A3 | ZSC | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
36 | ZSE-DO1043-A4 | ZSE | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
37 | ZSE-DO1043-A5 | ZSE | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
38 | ZSO-DO1043-A1 | ZSO | DO1043-A1 | BURNER(A) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
39 | ZSO-DO1043-A2 | ZSO | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
40 | ZSO-FA1043-A | ZSO | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
41 | ZSO-PA1043-A2 | ZSO | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
42 | ZSO-PA1043-A3 | ZSO | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
43 | ZSR-DO1043-A4 | ZSR | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
44 | ZSR-DO1043-A5 | ZSR | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
45 | ZT-DO1043-A3 | ZT | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,2/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
46 | ZT-FA1043-A | ZT | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,2/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
47 | BT-DO1043-B | BT | DO1043-B | #1 BURNER(B) COMPACT FLAME DETECTOR | PD-022,3/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0
48 | FCV-DO1043-B3 | FCV | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE | PD-022,3/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0
49 | FE-DO1043-B | FE | DO1043-B | #1 BURNER(B) DIESEL OIL FLOW ELEMENT | PD-022,3/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1
50 | FT-DO1043-B | FT | DO1043-B | #1 BURNER(B) DIESEL OIL FLOW TRANSMITTER | PD-022,3/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
51 | MCV-FA1043-B | MCV | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,3/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1
52 | PG-DO1043-B | PG | DO1043-B | #1 BURNER(B) DIESEL OIL PRESSURE GAUGE | PD-022,3/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
53 | PG-DO1043-B2 | PG | DO1043-B2 | #1 BURNER(B) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,3/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
54 | PG-FA1043-B | PG | FA1043-B | #1 BURNER(B) AIR PRESSURE GAUGE | PD-022,3/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
55 | PG-PA1043-B1 | PG | PA1043-B1 | #1 BURNER(B) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,3/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
56 | PG-PA1043-B2 | PG | PA1043-B2 | #1 BURNER(B) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,3/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
57 | PRV-PA1043-B | PRV | PA1043-B | #1 BURNER(B) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,3/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1
58 | PRV-PA1043-B1 | PRV | PA1043-B1 | #1 BURNER(B) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,3/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
59 | PSH-DO1043-B1 | PSH | DO1043-B1 | #1 BURNER(B) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,3/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
60 | PSL-PA1043-B1 | PSL | PA1043-B1 | #1 BURNER(B) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,3/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
61 | PT-DO1043-B2 | PT | DO1043-B2 | #1 BURNER(B) DIESEL OIL PRESSURE TRANSMITTER | PD-022,3/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
62 | SV-DO1043-B1 | SV | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
63 | SV-DO1043-B2 | SV | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
64 | SV-PA1043-B2 | SV | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
65 | SV-PA1043-B3 | SV | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
66 | SVE-DO1043-B4 | SVE | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 EXTRENDING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
67 | SVE-DO1043-B5 | SVE | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 EXTRENDING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
68 | SVR-DO1043-B5 | SVR | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
69 | TS-FA1043-B | TS | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
70 | XV-DO1043-B1 | XV | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
71 | XV-DO1043-B2 | XV | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
72 | XV-PA1043-B2 | XV | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
73 | XV-PA1043-B3 | XV | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
74 | ZS-DO1043-B3 | ZS | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
75 | ZS1-FA1043-B | ZS1 | FA1043-B | #1 BURNER(B) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
76 | ZS2-FA1043-B | ZS2 | FA1043-B | #1 BURNER(B) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
77 | ZSC-DO1043-B1 | ZSC | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
78 | ZSC-DO1043-B2 | ZSC | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
79 | ZSC-FA1043-B | ZSC | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
80 | ZSC-PA1043-B2 | ZSC | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
81 | ZSC-PA1043-B3 | ZSC | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
82 | ZSE-DO1043-B4 | ZSE | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
83 | ZSE-DO1043-B5 | ZSE | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
84 | ZSO-DO1043-B1 | ZSO | DO1043-B1 | BURNER(B) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
85 | ZSO-DO1043-B2 | ZSO | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
86 | ZSO-FA1043-B | ZSO | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
87 | ZSO-PA1043-B2 | ZSO | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
88 | ZSO-PA1043-B3 | ZSO | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
89 | ZSR-DO1043-B4 | ZSR | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
90 | ZSR-DO1043-B5 | ZSR | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
91 | ZT-DO1043-B3 | ZT | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,3/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
92 | ZT-FA1043-B | ZT | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,3/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
93 | BT-DO1043-C | BT | DO1043-C | #1 BURNER(C) COMPACT FLAME DETECTOR | PD-022,4/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0
94 | FCV-DO1043-C3 | FCV | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE | PD-022,4/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0
95 | FE-DO1043-C | FE | DO1043-C | #1 BURNER(C) DIESEL OIL FLOW ELEMENT | PD-022,4/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1
96 | FT-DO1043-C | FT | DO1043-C | #1 BURNER(C) DIESEL OIL FLOW TRANSMITTER | PD-022,4/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
97 | MCV-FA1043-C | MCV | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,4/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1
98 | PG-DO1043-C | PG | DO1043-C | #1 BURNER(C) DIESEL OIL PRESSURE GAUGE | PD-022,4/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
99 | PG-DO1043-C2 | PG | DO1043-C2 | #1 BURNER(C) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,4/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
100 | PG-FA1043-C | PG | FA1043-C | #1 BURNER(C) AIR PRESSURE GAUGE | PD-022,4/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
101 | PG-PA1043-C1 | PG | PA1043-C1 | #1 BURNER(C) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,4/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
102 | PG-PA1043-C2 | PG | PA1043-C2 | #1 BURNER(C) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,4/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
103 | PRV-PA1043-C | PRV | PA1043-C | #1 BURNER(C) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,4/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1
104 | PRV-PA1043-C1 | PRV | PA1043-C1 | #1 BURNER(C) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,4/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
105 | PSH-DO1043-C1 | PSH | DO1043-C1 | #1 BURNER(C) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,4/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
106 | PSL-PA1043-C1 | PSL | PA1043-C1 | #1 BURNER(C) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,4/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
107 | PT-DO1043-C2 | PT | DO1043-C2 | #1 BURNER(C) DIESEL OIL PRESSURE TRANSMITTER | PD-022,4/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
108 | SV-DO1043-C1 | SV | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
109 | SV-DO1043-C2 | SV | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
110 | SV-PA1043-C2 | SV | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
111 | SV-PA1043-C3 | SV | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
112 | SVE-DO1043-C4 | SVE | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 RETRACTING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
113 | SVE-DO1043-C5 | SVE | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
114 | SVR-DO1043-C5 | SVR | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
115 | TS-FA1043-C | TS | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
116 | XV-DO1043-C1 | XV | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
117 | XV-DO1043-C2 | XV | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
118 | XV-PA1043-C2 | XV | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
119 | XV-PA1043-C3 | XV | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
120 | ZS-DO1043-C3 | ZS | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
121 | ZS1-FA1043-C | ZS1 | FA1043-C | #1 BURNER(C) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
122 | ZS2-FA1043-C | ZS2 | FA1043-C | #1 BURNER(C) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
123 | ZSC-DO1043-C1 | ZSC | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
124 | ZSC-DO1043-C2 | ZSC | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
125 | ZSC-FA1043-C | ZSC | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
126 | ZSC-PA1043-C2 | ZSC | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
127 | ZSC-PA1043-C3 | ZSC | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
128 | ZSE-DO1043-C4 | ZSE | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
129 | ZSE-DO1043-C5 | ZSE | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
130 | ZSO-DO1043-C1 | ZSO | DO1043-C1 | BURNER(C) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
131 | ZSO-DO1043-C2 | ZSO | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
132 | ZSO-FA1043-C | ZSO | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
133 | ZSO-PA1043-C2 | ZSO | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
134 | ZSO-PA1043-C3 | ZSO | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
135 | ZSR-DO1043-C4 | ZSR | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
136 | ZSR-DO1043-C5 | ZSR | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
137 | ZT-DO1043-C3 | ZT | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,4/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
138 | ZT-FA1043-C | ZT | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,4/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
139 | BT-DO1043-D | BT | DO1043-D | #1 BURNER(D) COMPACT FLAME DETECTOR | PD-022,5/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0
140 | FCV-DO1043-D3 | FCV | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE | PD-022,5/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0
141 | FE-DO1043-D | FE | DO1043-D | #1 BURNER(D) DIESEL OIL FLOW ELEMENT | PD-022,5/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1
142 | FT-DO1043-D | FT | DO1043-D | #1 BURNER(D) DIESEL OIL FLOW TRANSMITTER | PD-022,5/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
143 | MCV-FA1043-D | MCV | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,5/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1
144 | PG-DO1043-D | PG | DO1043-D | #1 BURNER(D) DIESEL OIL PRESSURE GAUGE | PD-022,5/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
145 | PG-DO1043-D2 | PG | DO1043-D2 | #1 BURNER(D) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,5/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
146 | PG-FA1043-D | PG | FA1043-D | #1 BURNER(D) AIR PRESSURE GAUGE | PD-022,5/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
147 | PG-PA1043-D1 | PG | PA1043-D1 | #1 BURNER(D) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,5/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
148 | PG-PA1043-D2 | PG | PA1043-D2 | #1 BURNER(D) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,5/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1
149 | PRV-PA1043-D | PRV | PA1043-D | #1 BURNER(D) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,5/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1
150 | PRV-PA1043-D1 | PRV | PA1043-D1 | #1 BURNER(D) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,5/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK
151 | PSH-DO1043-D1 | PSH | DO1043-D1 | #1 BURNER(D) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,5/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
152 | PSL-PA1043-D1 | PSL | PA1043-D1 | #1 BURNER(D) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,5/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
153 | PT-DO1043-D2 | PT | DO1043-D2 | #1 BURNER(D) DIESEL OIL PRESSURE TRANSMITTER | PD-022,5/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
154 | SV-DO1043-D1 | SV | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
155 | SV-DO1043-D2 | SV | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
156 | SV-PA1043-D2 | SV | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
157 | SV-PA1043-D3 | SV | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
158 | SVE-DO1043-D4 | SVE | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 RETRACTING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
159 | SVE-DO1043-D5 | SVE | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
160 | SVR-DO1043-D5 | SVR | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0
161 | TS-FA1043-D | TS | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
162 | XV-DO1043-D1 | XV | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
163 | XV-DO1043-D2 | XV | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
164 | XV-PA1043-D2 | XV | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
165 | XV-PA1043-D3 | XV | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0
166 | ZS-DO1043-D3 | ZS | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
167 | ZS1-FA1043-D | ZS1 | FA1043-D | #1 BURNER(D) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
168 | ZS2-FA1043-D | ZS2 | FA1043-D | #1 BURNER(D) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
169 | ZSC-DO1043-D1 | ZSC | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
170 | ZSC-DO1043-D2 | ZSC | DO1043-D2 | #1 BURNER(D) FUEL OILPNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
171 | ZSC-FA1043-D | ZSC | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
172 | ZSC-PA1043-D2 | ZSC | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
173 | ZSC-PA1043-D3 | ZSC | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
174 | ZSE-DO1043-D4 | ZSE | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
175 | ZSE-DO1043-D5 | ZSE | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
176 | ZSO-DO1043-D1 | ZSO | DO1043-D1 | BURNER(D) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
177 | ZSO-DO1043-D2 | ZSO | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
178 | ZSO-FA1043-D | ZSO | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1
179 | ZSO-PA1043-D2 | ZSO | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
180 | ZSO-PA1043-D3 | ZSO | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
181 | ZSR-DO1043-D4 | ZSR | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
182 | ZSR-DO1043-D5 | ZSR | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
183 | ZT-DO1043-D3 | ZT | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,5/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0
184 | ZT-FA1043-D | ZT | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,5/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1

## FLUIDIZING AIR
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
FLUIDIZING AIR SYSTEM
1 | DPSH-FA1055-A | DPSH | FA1055-A | #1 FLUIDIZING AIR BLOWER(A) INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
2 | DPSH-FA1055-B | DPSH | FA1055-B | #1 FLUIDIZING AIR BLOWER(B) INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
3 | FCV-FA1055-A1 | FCV | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE | PD-054 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (BLOWER) |  | 0
4 | FCV-FA1055-B1 | FCV | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE | PD-054 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (BLOWER) |  | 0
5 | LG-FA1055-A1 | LG | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) OIL LEVEL GAUGE(OIL CUP)-1 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1
6 | LG-FA1055-A2 | LG | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) OIL LEVEL GAUGE(OIL CUP)-2 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1
7 | LG-FA1055-B1 | LG | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) OIL LEVEL GAUGE(OIL CUP)-1 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1
8 | LG-FA1055-B2 | LG | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) OIL LEVEL GAUGE(OIL CUP)-2 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1
9 | PG-FA1055-A | PG | FA1055-A | #1 FLUIDIZING AIR BLOWER(A) PRESSURE GAUGE | PD-054 | - | - | 0~1Kg/c㎡G | - | - | - | - | PACKAGE (BLOWER) |  | 0
10 | PG-FA1055-B | PG | FA1055-B | #1 FLUIDIZING AIR BLOWER(B) PRESSURE GAUGE | PD-054 | - | - | 0~1Kg/c㎡G | - | - | - | - | PACKAGE (BLOWER) |  | 0
11 | SV-FA1055-A2 | SV | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0
12 | SV-FA1055-A3 | SV | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0
13 | SV-FA1055-B2 | SV | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0
14 | SV-FA1055-B3 | SV | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0
15 | TE-FA1055-A1 | TE | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
16 | TE-FA1055-A2 | TE | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
17 | TE-FA1055-A3 | TE | FA1055-A3 | #1 FLUIDIZING AIR BLOWER(A) MOTOR FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
18 | TE-FA1055-A4 | TE | FA1055-A4 | #1 FLUIDIZING AIR BLOWER(A) MOTOR REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
19 | TE-FA1055-AU1 | TE | FA1055-AU1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-U1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
20 | TE-FA1055-AU2 | TE | FA1055-AU2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-U2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
21 | TE-FA1055-AV1 | TE | FA1055-AV1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-V1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
22 | TE-FA1055-AV2 | TE | FA1055-AV2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-V2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
23 | TE-FA1055-AW1 | TE | FA1055-AW1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE -W1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
24 | TE-FA1055-AW2 | TE | FA1055-AW2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE -W2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
25 | TE-FA1055-B1 | TE | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
26 | TE-FA1055-B2 | TE | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
27 | TE-FA1055-B3 | TE | FA1055-B3 | #1 FLUIDIZING AIR BLOWER(B) MOTOR FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
28 | TE-FA1055-B4 | TE | FA1055-B4 | #1 FLUIDIZING AIR BLOWER(B) MOTOR REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
29 | TE-FA1055-BU1 | TE | FA1055-BU1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-U1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
30 | TE-FA1055-BU2 | TE | FA1055-BU2 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-U2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
31 | TE-FA1055-BV1 | TE | FA1055-BV1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-V1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
32 | TE-FA1055-BV1 | TE | FA1055-BV1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-V2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
33 | TE-FA1055-BW1 | TE | FA1055-BW1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-W1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
34 | TE-FA1055-BW2 | TE | FA1055-BW2 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-W2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0
35 | VT-FA1055-A1 | VT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) REAR BEARING VIBRATION TRANSMITTER-1 | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
36 | VT-FA1055-A2 | VT | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
37 | VT-FA1055-A3 | VT | FA1055-A3 | #1 FLUIDIZING AIR BLOWER(A) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
38 | VT-FA1055-A4 | VT | FA1055-A4 | #1 FLUIDIZING AIR BLOWER(A) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
39 | VT-FA1055-B1 | VT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) REAR BEARING VIBRATION TRANSMITTER-1 | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
40 | VT-FA1055-B2 | VT | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
41 | VT-FA1055-B3 | VT | FA1055-B3 | #1 FLUIDIZING AIR BLOWER(B) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
42 | VT-FA1055-B4 | VT | FA1055-B4 | #1 FLUIDIZING AIR BLOWER(B) MOTOR RAER BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
43 | XV-FA1055-A2 | XV | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0
44 | XV-FA1055-A3 | XV | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0
45 | XV-FA1055-B2 | XV | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0
46 | XV-FA1055-B3 | XV | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0
47 | ZSC-FA1055-A1 | ZSC | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
48 | ZSC-FA1055-A2 | ZSC | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
49 | ZSC-FA1055-A3 | ZSC | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
50 | ZSC-FA1055-B1 | ZSC | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
51 | ZSC-FA1055-B2 | ZSC | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
52 | ZSC-FA1055-B3 | ZSC | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
53 | ZSO-FA1055-A1 | ZSO | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
54 | ZSO-FA1055-A2 | ZSO | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
55 | ZSO-FA1055-A3 | ZSO | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
56 | ZSO-FA1055-B1 | ZSO | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
57 | ZSO-FA1055-B2 | ZSO | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
58 | ZSO-FA1055-B3 | ZSO | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
59 | ZT-FA1055-A1 | ZT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE POSITION TRANSMITTER | PD-054 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0
60 | ZT-FA1055-B1 | ZT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE POSITION TRANSMITTER | PD-054 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0

## HYPO-CHLORINATED DOSING
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
HYPO-CHLORINATED DOSING SYSTEM
1 | LG-0762A | LG | 0762A | HYPO-CHLORINATED DOSING SYSTEM TANK T-0762A LEVEL GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1
2 | LG-0762B | LG | 0762B | HYPO-CHLORINATED DOSING SYSTEM TANK T-0762B LEVEL GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1
3 | PG-0761 | PG | 0761 | HYPO-CHLORINATED DOSING SYSTEM TRANSFER PUMP P-0761 DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1
4 | PG-0766 | PG | 0766 | HYPO-CHLORINATED DOSING PIPE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1
5 | PG-0762A | PG | 0762A | HYPO-CHLORINATED DOSING SYSTEM NaOCL DOSING PUMP P-0762A DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1
6 | PG-0762B | PG | 0762B | HYPO-CHLORINATED DOSING SYSTEM NaOCL DOSING PUMP P-0762B DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1

## INDUCED DRAFT FAN
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
INDUCED DRAFT FAN
1 | DPG-LO1756-1 | DPG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE GAUGE (MAINTENANCE) | PD-051 | - | - | 0.61 Kg/c㎡ | - | - | - | - | PACKAGE (IDF) |  | 0
2 | DPG-LO1756-2 | DPG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE GAUGE OF DUPLEX FILTER | PD-051 | - | - | 0~1.1 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 1
3 | DPS-LO1756 | DPS | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE SWITCH HIGH OF DUPLEX FILTER | PD-051 | - | - | 0.20~2.04 Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0
4 | LG-LO1756-2 | LG | LO1756-2 | #1 INDUCED DRAFT FAN OIL LEVEL GAUGE | PD-051 | - | - | - | - | - | - | - | PACKAGE (IDF) |  | 0
5 | PCD-FG1056-1 | PCD | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE CONTROL DAMPER | PD-051 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (IDF) |  | 0
6 | PG-LO1756-1 | PG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL PRESSURE GAUGE AT UPSTREAM OF COUPLING | PD-051 | - | - | 0~4.08 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 0
7 | PG-LO1756-2 | PG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL PRESSURE GAUGE AT DOWNSTREAM OF LUBE OIL ORIFICE | PD-051 | - | - | 0~1.1 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 0
8 | PSL-LO1756 | PSL | LO1756 | #1 INDUCED DRAFT FAN LUBE OIL PRESSURE SWITCH LOW AT DOWNSTREAM OF LUBE OIL FILTER | PD-051 | - | - | 0~2.55 Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0
9 | PSLL-LO1756 | PSLL | LO1756 | #1 INDUCED DRAFT FAN LUBE OIL PRESSURE SWITCH LOW-LOW AT DOWNSTREAM OF LUBE OIL FILTER | PD-051 | - | - | 0~2.55 Kg/c㎡G | DI | FIELD | ARP | - | PACKAGE (IDF) |  | 0
10 | SE-LO1756 | SE | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING PICK UP SPEED | PD-051 | - | - | - | - | - | - | - | PACKAGE (IDF) |  | 0
11 | ST-LO1756 | ST | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING PICK UP SPEED TRANSMITTER | PD-051 | - | - | 1200rpm | WET 4~20mA | LCP | DCS | - | PACKAGE (IDF) |  | 0
12 | TE-FG1056-1 | TE | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
13 | TE-FG1056-2 | TE | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
14 | TE-FG1056-3 | TE | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
15 | TE-FG1056-4 | TE | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
16 | TE-FG1056-U1 | TE | FG1056-U1 | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
17 | TE-FG1056-U2 | TE | FG1056-U2 | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
18 | TE-FG1056-V1 | TE | FG1056-V1 | #1 INDUCED DRAFT FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
19 | TE-FG1056-V2 | TE | FG1056-V2 | #1 INDUCED DRAFT FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
20 | TE-FG1056-W1 | TE | FG1056-W1 | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
21 | TE-FG1056-W2 | TE | FG1056-W2 | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0
22 | TG-LO1756-1 | TG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE GAUGE AT UPSTREAM OF HEAT EXCHANGER | PD-051 | - | - | 0~150℃ | - | - | - | BI-METAL | PACKAGE (IDF) |  | 0
23 | TG-LO1756-2 | TG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE GAUGE AT DOWNSTREAM OF HEAT EXCHANGER | PD-051 | - | - | 0~150℃ | - | - | - | BI-METAL | PACKAGE (IDF) |  | 0
24 | TS-LO1756-1 | TS | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE SWITCH HIGH | PD-051 | - | - | 0~160℃ | DI | FIELD | DCS | CAPILLIARY | PACKAGE (IDF) |  | 0
25 | TS-LO1756-2 | TS | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE SWITCH HIGH-HIGH | PD-051 | - | - | 0~160℃ | DI | FIELD | ARP | CAPILLIARY | PACKAGE (IDF) |  | 0
26 | VT-FG1056-1 | VT | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0
27 | VT-FG1056-2 | VT | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0
28 | VT-FG1056-3 | VT | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0
29 | VT-FG1056-4 | VT | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0
30 | ZSC-FG1056-1 | ZSC | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE PNEUMATIC CONTROL DAMPER CLOSE POSITION SWITCH | PD-051 | - | - | - | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0
31 | ZSC-LO1756 | ZSC | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING COUPLING SCOOP TUBE POSITION(0%) | PD-051 | - | - | - | DI | LCP | DCS | - | PACKAGE (IDF) |  | 0
32 | ZSO-FG1056-1 | ZSO | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE PNEUMATIC CONTROL DAMPER OPEN POSITION SWITCH | PD-051 | - | - | - | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0
33 | ZSO-LO1756 | ZSO | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING SCOOP TUBE POSITION(100%) | PD-051 | - | - | - | DI | LCP | DCS | - | PACKAGE (IDF) |  | 0
34 | ZT-FG1056-1 | ZT | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE CONTROL DAMPER POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0
35 | ZT-LO1756 | ZT | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING SCOOP TUBE POSITION TRANSMITTER | PD-051 | - | - | 0~100% | WET 4~21mA | LCP | DCS | - | PACKAGE (IDF) |  | 0

## PRIMARY AIR FAN
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
PRIMARY AIR FAN
1 | MCV-FA1053-1 | MCV | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV | PD-052 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (PAF) |  | 0
2 | TE-FA1053-1 | TE | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
3 | TE-FA1053-2 | TE | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
4 | TE-FA1053-3 | TE | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
5 | TE-FA1053-4 | TE | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
6 | TE-FA1053-U1 | TE | FA1053-U1 | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
7 | TE-FA1053-U2 | TE | FA1053-U2 | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
8 | TE-FA1053-V1 | TE | FA1053-V1 | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
9 | TE-FA1053-V2 | TE | FA1053-V2 | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
10 | TE-FA1053-W1 | TE | FA1053-W1 | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
11 | TE-FA1053-W2 | TE | FA1053-W2 | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0
12 | TS-FA1053-1 | TS | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0
13 | VT-FA1053-1 | VT | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0
14 | VT-FA1053-2 | VT | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0
15 | VT-FA1053-3 | VT | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0
16 | VT-FA1053-4 | VT | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0
17 | ZSC-FA1053-1 | ZSC | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0
18 | ZSO-FA1053-1 | ZSO | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0
19 | ZT-FA1053-1 | ZT | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-052 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0

## PRIMARY AIR FAN LUBE OIL
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
PRIMARY AIR FAN LUBE OIL SYSTEM
1 | DPS-LO1753 | DPS | LO1753 | #1 PRIMARY AIR FAN INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-052 | - | - | 0~10Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0
2 | LSL-LO1753 | LSL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL LEVEL SWITCH | PD-052 | - | - | 270L(<240L) | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0
3 | LSLL-LO1753 | LSLL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL LEVEL SWITCH | PD-052 | - | - | 270L(<200L) | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0
4 | PG-LO1753-1 | PG | LO1753-1 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-1 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0
5 | PG-LO1753-2 | PG | LO1753-2 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-2 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0
6 | PG-LO1753-3 | PG | LO1753-3 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-3 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0
7 | PG-LO1753-4 | PG | LO1753-4 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-4 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0
8 | PG-LO1753-5 | PG | LO1753-5 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-5 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0
9 | PG-LO1753-6 | PG | LO1753-6 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-6 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0
10 | PSL-LO1753 | PSL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE LOW SWITCH | PD-052 | - | - | 0~10Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0
11 | PSLL-LO1753 | PSLL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE LOW LOW SWITCH | PD-052 | - | - | 0~6Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0
12 | TG-LO1753 | TG | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM TEMPERATURE GAUGE | PD-052 | - | - | 0~100℃ | - | - | - |  | PACKAGE (PAF) |  | 0
13 | TS-LO1753 | TS | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM TEMPERATURE SWITCH | PD-052 | - | - | 0~200℃ | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0

## SECONDARY AIR FAN
ITEM | TAG. NO. |  |  | FUNCTION | P&ID DWG NO. | DESIGN CONDITION |  | RANGE | SIGNAL | CONNECTION |  | TYPE | SUPPLY SCOPE | REMARKS | R
[6 empty] | P(Kg/c㎡G) | T( ℃ ) |  |  | FROM | TO |  |  |  | E
V
SECONDARY AIR FAN
1 | MCV-FA1005 | MCV | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
2 | MCV-FA1006 | MCV | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
3 | MCV-FA1007 | MCV | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
4 | MCV-FA1008 | MCV | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
5 | MCV-FA1009 | MCV | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
6 | MCV-FA1010 | MCV | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
7 | MCV-FA1011 | MCV | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
8 | MCV-FA1012 | MCV | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
9 | MCV-FA1013 | MCV | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
10 | MCV-FA1014 | MCV | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
11 | MCV-FA1015 | MCV | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
12 | MCV-FA1016 | MCV | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
13 | MCV-FA1017 | MCV | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
14 | MCV-FA1018 | MCV | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
15 | MCV-FA1019 | MCV | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
16 | MCV-FA1020 | MCV | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
17 | MCV-FA1021 | MCV | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
18 | MCV-FA1022 | MCV | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
19 | MCV-FA1023 | MCV | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
20 | MCV-FA1024 | MCV | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
21 | MCV-FA1025 | MCV | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
22 | MCV-FA1026 | MCV | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0
23 | MCV-FA1054-1 | MCV | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (SAF) |  | 0
24 | TE-FA1054-1 | TE | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
25 | TE-FA1054-2 | TE | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
26 | TE-FA1054-3 | TE | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
27 | TE-FA1054-4 | TE | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
28 | TE-FA1054-U1 | TE | FA1054-U1 | #1 SECONDARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
29 | TE-FA1054-U2 | TE | FA1054-U2 | #1 SECONDARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
30 | TE-FA1054-V1 | TE | FA1054-V1 | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
31 | TE-FA1054-V2 | TE | FA1054-V2 | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
32 | TE-FA1054-W1 | TE | FA1054-W1 | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
33 | TE-FA1054-W2 | TE | FA1054-W2 | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0
34 | TS-FA1005 | TS | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
35 | TS-FA1006 | TS | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
36 | TS-FA1007 | TS | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
37 | TS-FA1008 | TS | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
38 | TS-FA1009 | TS | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
39 | TS-FA1010 | TS | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
40 | TS-FA1011 | TS | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
41 | TS-FA1012 | TS | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
42 | TS-FA1013 | TS | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
43 | TS-FA1014 | TS | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
44 | TS-FA1015 | TS | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
45 | TS-FA1016 | TS | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
46 | TS-FA1017 | TS | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
47 | TS-FA1018 | TS | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
48 | TS-FA1019 | TS | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
49 | TS-FA1020 | TS | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
50 | TS-FA1021 | TS | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
51 | TS-FA1022 | TS | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
52 | TS-FA1023 | TS | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
53 | TS-FA1024 | TS | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
54 | TS-FA1025 | TS | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
55 | TS-FA1026 | TS | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
56 | TS-FA1054-1 | TS | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0
57 | VT-FA1054-1 | VT | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0
58 | VT-FA1054-2 | VT | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0
59 | VT-FA1054-3 | VT | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0
60 | VT-FA1054-4 | VT | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0
61 | ZSC-FA1005 | ZSC | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
62 | ZSC-FA1006 | ZSC | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
63 | ZSC-FA1007 | ZSC | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
64 | ZSC-FA1008 | ZSC | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
65 | ZSC-FA1009 | ZSC | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
66 | ZSC-FA1010 | ZSC | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
67 | ZSC-FA1011 | ZSC | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
68 | ZSC-FA1012 | ZSC | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
69 | ZSC-FA1013 | ZSC | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
70 | ZSC-FA1014 | ZSC | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
71 | ZSC-FA1015 | ZSC | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
72 | ZSC-FA1016 | ZSC | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
73 | ZSC-FA1017 | ZSC | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
74 | ZSC-FA1018 | ZSC | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
75 | ZSC-FA1019 | ZSC | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
76 | ZSC-FA1020 | ZSC | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
77 | ZSC-FA1021 | ZSC | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
78 | ZSC-FA1022 | ZSC | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
79 | ZSC-FA1023 | ZSC | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
80 | ZSC-FA1024 | ZSC | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
81 | ZSC-FA1025 | ZSC | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
82 | ZSC-FA1026 | ZSC | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
83 | ZSC-FA1054-1 | ZSC | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0
84 | ZSO-FA1005 | ZSO | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
85 | ZSO-FA1006 | ZSO | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
86 | ZSO-FA1007 | ZSO | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
87 | ZSO-FA1008 | ZSO | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
88 | ZSO-FA1009 | ZSO | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
89 | ZSO-FA1010 | ZSO | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
90 | ZSO-FA1011 | ZSO | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
91 | ZSO-FA1012 | ZSO | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
92 | ZSO-FA1013 | ZSO | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
93 | ZSO-FA1014 | ZSO | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
94 | ZSO-FA1015 | ZSO | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
95 | ZSO-FA1016 | ZSO | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
96 | ZSO-FA1017 | ZSO | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
97 | ZSO-FA1018 | ZSO | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
98 | ZSO-FA1019 | ZSO | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
99 | ZSO-FA1020 | ZSO | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
100 | ZSO-FA1021 | ZSO | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
101 | ZSO-FA1022 | ZSO | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
102 | ZSO-FA1023 | ZSO | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
103 | ZSO-FA1024 | ZSO | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
104 | ZSO-FA1025 | ZSO | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
105 | ZSO-FA1026 | ZSO | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0
106 | ZSO-FA1054-1 | ZSO | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0
107 | ZT-FA1005 | ZT | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
108 | ZT-FA1006 | ZT | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
109 | ZT-FA1007 | ZT | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
110 | ZT-FA1008 | ZT | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
111 | ZT-FA1009 | ZT | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
112 | ZT-FA1010 | ZT | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
113 | ZT-FA1011 | ZT | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
114 | ZT-FA1012 | ZT | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
115 | ZT-FA1013 | ZT | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
116 | ZT-FA1014 | ZT | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
117 | ZT-FA1015 | ZT | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
118 | ZT-FA1016 | ZT | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
119 | ZT-FA1017 | ZT | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
120 | ZT-FA1018 | ZT | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
121 | ZT-FA1019 | ZT | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
122 | ZT-FA1020 | ZT | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
123 | ZT-FA1021 | ZT | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
124 | ZT-FA1022 | ZT | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
125 | ZT-FA1023 | ZT | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
126 | ZT-FA1024 | ZT | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
127 | ZT-FA1025 | ZT | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
128 | ZT-FA1026 | ZT | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0
129 | ZT-FA1054-1 | ZT | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0

## MASTER (2)
[6 empty] | DESIGN CONDITION |  |  |  | CONNECTION |  |  |  |  | R
E
ITEM | TAG. NO. |  |  |  | P&ID DWG NO. | P(Kg/c㎡G) | T( ℃ ) | RANGE | SIGNAL | FROM | TO | TYPE | SUPPLY SCOPE | REMARKS | V |  | TYPE/PACKAGE
22 | AT-FG1057-1 | AT | FG1057-1 | #1 STACK FLUE GAS SOX ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
23 | AT-FG1057-2 | AT | FG1057-2 | #1 STACK FLUE GAS NOX ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
24 | AT-FG1057-3 | AT | FG1057-3 | #1 STACK FLUE GAS CO ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
25 | AT-FG1057-4 | AT | FG1057-4 | #1 STACK FLUE GAS O2 ANALYZER | PD-051 | ±410mmAq | 200 | 0~21% | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
26 | AT-FG1057-5 | AT | FG1057-5 | #1 STACK FLUE GAS DUST ANALYZER | PD-051 | ±410mmAq | 200 | 0~1000 mg/m3 | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
27 | AT-FG1057-6 | AT | FG1057-6 | #1 STACK FLUE GAS OPACITY ANALYZER | PD-051 | ±410mmAq | 200 | 0~100% | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
28 | AT-FG1122 | AT | FG1122 | #1 ECONOMIZER OUTLET FLUE GAS O2 (A) | PD-051 | ±890mmAq | 371 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0 |  | AT
29 | AT-FG1123 | AT | FG1123 | #1 ECONOMIZER OUTLET FLUE GAS O2 (B) | PD-051 | ±890mmAq | 371 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0 |  | AT
30 | AT-FG1131 | AT | FG1131 | #1 AIR PRE-HEATER GAS OUTLET FLUE GAS O2 (C) | PD-051 | ±890mmAq | 200 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0 |  | AT
1 | #VALUE! | AT | SP1001 | #1 DEAERATOR UPSTREAM WATER PH | PD-044 | 24 | 65 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
2 | AT-SP1002 | AT | SP1002 | #1 DEAERATOR UPSTREAM WATER CATION CONDUCTIVITY | PD-044 | 24 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
3 | AT-SP1003 | AT | SP1003 | #1 DEAERATOR OUTLET WATER PH | PD-044 | 9 | 180 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
4 | AT-SP1004 | AT | SP1004 | #1 DEAERATOR OUTLET WATER DISSOLVED OXYGEN | PD-044 | 9 | 180 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
5 | AT-SP1005 | AT | SP1005 | #1 DEAERATOR OUTLET WATER CATION CONDUCTIVITY | PD-044 | 9 | 180 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
6 | AT-SP1006 | AT | SP1006 | #1 MAKE-UP WATER PUMP OUTLET WATER PH | PD-044 | 10 | 65 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
7 | AT-SP1007 | AT | SP1007 | #1 MAKE-UP WATER PUMP OUTLET WATER SPECIFIC CONDUCTIVITY | PD-044 | 10 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
8 | AT-SP1008 | AT | SP1008 | #1 MAKE-UP WATER PUMP OUTLET WATER SILICA | PD-044 | 10 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
9 | AT-SP1009 | AT | SP1009 | #1 ECONOMIZER INLET WATER PH | PD-044 | 215 | 275 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
10 | AT-SP1010 | AT | SP1010 | #1 ECONOMIZER INLET WATER DISSOLVED OXYGEN | PD-044 | 215 | 275 | 0~20ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
11 | AT-SP1011 | AT | SP1011 | #1 DRUM WATER(BLOW DOWN) PH | PD-044 | 148 | 343 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
12 | AT-SP1012 | AT | SP1012 | #1 DRUM WATER(BLOW DOWN) SPECIFIC CONDUCTIVITY | PD-044 | 148 | 343 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
13 | AT-SP1013 | AT | SP1013 | #1 DRUM WATER(BLOW DOWN)SILICA | PD-044 | 148 | 343 | 0~500ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
14 | AT-SP1014 | AT | SP1014 | #1 SATURATED STEAM SPECIFIC CONDUCTIVITY | PD-044 | 148 | 343 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
15 | AT-SP1015 | AT | SP1015 | #1 SATURATED STEAM SILICA | PD-044 | 148 | 343 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
16 | AT-SP1016 | AT | SP1016 | #1 MAIN STEAM PH | PD-044 | 144 | 550 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
17 | AT-SP1017 | AT | SP1017 | #1 MAIN STEAM SILICA | PD-044 | 144 | 550 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
18 | AT-SP1018 | AT | SP1018 | #1 CONDENSATE PUMP OUTLET WATER CATION CONDUCTIVITY-1 | PD-044 | 24 | 65.6 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
19 | AT-SP1019 | AT | SP1019 | #1 CONDENSATE PUMP OUTLET WATER CATION CONDUCTIVITY-2 | PD-044 | 24 | 65.6 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
20 | AT-SP1020 | AT | SP1020 | #1 CONDENSATE PUMP OUTLET WATER SODIUM | PD-044 | 24 | 65.6 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
21 | AT-SP1021 | AT | SP1021 | #1 MAIN STEAM LINE CATION CONDUCTIVITY | PD-044 | 144 | 550 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
1+34:5234:61E3434:4234:71E343434:42 | BT-DO1043-A | BT | DO1043-A | #1 BURNER(A) COMPACT FLAME DETECTOR | PD-022,2/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
47 | BT-DO1043-B | BT | DO1043-B | #1 BURNER(B) COMPACT FLAME DETECTOR | PD-022,3/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
93 | BT-DO1043-C | BT | DO1043-C | #1 BURNER(C) COMPACT FLAME DETECTOR | PD-022,4/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
139 | BT-DO1043-D | BT | DO1043-D | #1 BURNER(D) COMPACT FLAME DETECTOR | PD-022,5/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
24 | DPG-FG1052-1 | DPG | FG1052-1 | #1 SECONDARY AIR/GAS HOT END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
25 | DPG-FG1052-2 | DPG | FG1052-2 | #1 PRIMARY AIR/GAS HOT END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
26 | DPG-FG1052-3 | DPG | FG1052-3 | #1 SECONDARY AIR/GAS COLD END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
27 | DPG-FG1052-4 | DPG | FG1052-4 | #1 PRIMARY AIR/GAS COLD END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
1 | DPG-FW1115-A | DPG | FW1115-A | #1 BFP(A) SUCTION STRAINER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~0.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
2 | DPG-FW1115-B | DPG | FW1115-B | #1 BFP(B) SUCTION STRAINER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~0.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
3 | DPG-LO1115-A | DPG | LO1115-A | #1 BFP(A) LUBE OIL INLET FILTER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~1.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
4 | DPG-LO1115-B | DPG | LO1115-B | #1 BFP(B) LUBE OIL INLET FILTER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~1.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
1 | DPG-LO1756-1 | DPG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE GAUGE (MAINTENANCE) | PD-051 | - | - | 0.61 Kg/c㎡ | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
2 | DPG-LO1756-2 | DPG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE GAUGE OF DUPLEX FILTER | PD-051 | - | - | 0~1.1 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 1 |  | INDUCED DRAFT FAN
1 | DPSH-FA1055-A | DPSH | FA1055-A | #1 FLUIDIZING AIR BLOWER(A) INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
2 | DPSH-FA1055-B | DPSH | FA1055-B | #1 FLUIDIZING AIR BLOWER(B) INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
1 | DPS-LO1753 | DPS | LO1753 | #1 PRIMARY AIR FAN INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-052 | - | - | 0~10Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
3 | DPS-LO1756 | DPS | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE SWITCH HIGH OF DUPLEX FILTER | PD-051 | - | - | 0.20~2.04 Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
1 | DPT-CD1001 | DPT | CD1001 | #1 CONDENSATE PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-016 | 3.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | DPT
2 | DPT-CD1002 | DPT | CD1002 | #1 CONDENSATE PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-016 | 3.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | DPT
9 | DPT-CW1108-A | DPT | CW1108-A | #1 AUXILIARY COOLING WATER PUMP A STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
10 | DPT-CW1108-B | DPT | CW1108-B | #1 AUXILIARY COOLING WATER PUMP B STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
11 | DPT-DO0001 | DPT | DO0001 | DIESEL OIL PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-022,1/5 | 7 | 70 | 0~1.0 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | DPT
17 | DPT-FG1052-5 | DPT | FG1052-5 | #1 AIR PREHEATER DIFFERENTIAL PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~3300 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
18 | DPT-FG1081 | DPT | FG1081 | #1 OVERALL FURNACE DIFFERENTIAL PRESSURE TRANSMITTER (A) | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
19 | DPT-FG1082 | DPT | FG1082 | #1 OVERALL FURNACE DIFFERENTIAL PRESSURE TRANSMITTER (B) | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
20 | DPT-FG1083 | DPT | FG1083 | #1 MIDDLE/UPPER FURNACE DIFFERENTIAL PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 1200 | -1500~1500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
21 | DPT-FG1084 | DPT | FG1084 | #1 FURNACE GRATE DIFFERENTIAL PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
22 | DPT-FG1183 | DPT | FG1183 | #1 MIDDLE/UPPER FURNACE DIFFERENTIAL PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 1200 | -1500~1500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI | NEW ADDED | 0 |  | DPT
23 | DPT-FG1184 | DPT | FG1184 | #1 FURNACE GRATE DIFFERENTIAL PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI | NEW ADDED | 0 |  | DPT
3 | DPT-FW1115-A | DPT | FW1115-A | #1 BFP(A) SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-017 | - | - | 0~0.6 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | PACKAGE (BFP) |  | 0 |  | DPT
4 | DPT-FW1115-B | DPT | FW1115-B | #1 BFP(B) SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-017 | - | - | 0~0.6 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | PACKAGE (BFP) |  | 0 |  | DPT
15 | DPT-IW0715-A | DPT | IW0715-A | INDUSTRIAL WATER PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-025 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
16 | DPT-IW0715-B | DPT | IW0715-B | INDUSTRIAL WATER PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-025 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
12 | DPT-MU0709-A | DPT | MU0709-A | MAKE-UP PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
13 | DPT-MU0709-B | DPT | MU0709-B | MAKE-UP PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
14 | DPT-MU0709-C | DPT | MU0709-C | MAKE-UP PUMP C SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
5 | DPT-SW1111 | DPT | SW1111 | #1 BALL SEPARATOR L-1111 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~100mBar | AI 4~20mA | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | DPT
6 | DPT-SW1112 | DPT | SW1112 | #1 BALL SEPARATOR L-1112 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~100mBar | AI 4~20mA | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | DPT
7 | DPT-SW1502 | DPT | SW1502 | #1 DEBRIS FILTER S-1502 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~2000 mmH2O | AI 4~20mA | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | DPT
8 | DPT-SW1504 | DPT | SW1504 | #1 DEBRIS FILTER S-1504 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~2000 mmH2O | AI 4~20mA | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | DPT
9 | FCV-CD1120 | FCV | CD1120 | #1 CONDENSATE SYSTEM MINIMUM FLOW RECIRCULATION CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
10 | FCV-CD1121 | FCV | CD1121 | #1 CONDENSATE POLISHIER FLOW CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
36 | FCV-DO1012 | FCV | DO1012 | #1 DIESEL OIL SUPPLY TO BURNER FLOW CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 1 |  | CV
2 | FCV-DO1043-A3 | FCV | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE | PD-022,2/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
48 | FCV-DO1043-B3 | FCV | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE | PD-022,3/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
94 | FCV-DO1043-C3 | FCV | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE | PD-022,4/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
140 | FCV-DO1043-D3 | FCV | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE | PD-022,5/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
3 | FCV-FA1055-A1 | FCV | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE | PD-054 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
4 | FCV-FA1055-B1 | FCV | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE | PD-054 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
17 | FCV-FW1130-1 | FCV | FW1130-1 | #1 BOILER FEEDWATER FLOW CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
18 | FCV-FW1130-2 | FCV | FW1130-2 | #1 BOILER FEEDWATER FLOW CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
2 | FE-CD1115 | FE | CD1115 | #1 LP TURBINE BYPASS SPRAY WATER FLOW ELEMENT | PD-016 | 24 | 65 | 0~46 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
3 | FE-CD1120 | FE | CD1120 | #1 CONDENSATE WATER FLOW ELEMENT | PD-016 | 24 | 65 | 0~400 | <5000 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
4 | FE-CD1121 | FE | CD1121 | #1 CONDESATE POLISHER SYSTEM INLET FLOW ELEMENT | PD-016 | 24 | 65 | 0~200 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
5 | FE-CD1122 | FE | CD1122 | #1 DEAERATOR IN CONDESATE FLOW ELEMENT | PD-016 | 24 | 200 | 0~450 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
3 | FE-DO1043-A | FE | DO1043-A | #1 BURNER(A) DIESEL OIL FLOW ELEMENT | PD-022,2/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
49 | FE-DO1043-B | FE | DO1043-B | #1 BURNER(B) DIESEL OIL FLOW ELEMENT | PD-022,3/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
95 | FE-DO1043-C | FE | DO1043-C | #1 BURNER(C) DIESEL OIL FLOW ELEMENT | PD-022,4/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
141 | FE-DO1043-D | FE | DO1043-D | #1 BURNER(D) DIESEL OIL FLOW ELEMENT | PD-022,5/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
23 | FE-FA1009-A1 | FE | FA1009-A1 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT A | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
24 | FE-FA1009-A2 | FE | FA1009-A2 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT B | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
25 | FE-FA1009-B1 | FE | FA1009-B1 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT A | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
26 | FE-FA1009-B2 | FE | FA1009-B2 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT B | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
15 | FE-FA1043-A | FE | FA1043-A | #1 START-UP BURNER(A) HOT SECONDARY AIR FLOW ELEMENT | PD-022,2/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
16 | FE-FA1043-B | FE | FA1043-B | #1 START-UP BURNER(B) HOT SECONDARY AIR FLOW ELEMENT | PD-022,3/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
17 | FE-FA1043-C | FE | FA1043-C | #1 START-UP BURNER(C) HOT SECONDARY AIR FLOW ELEMENT | PD-022,4/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
18 | FE-FA1043-D | FE | FA1043-D | #1 START-UP BURNER(D) HOT SECONDARY AIR FLOW ELEMENT | PD-022,5/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
22 | FE-FA1055 | FE | FA1055 | #1 FLUIDIZING AIR BLOWER OUTLET COMMON FLOW ELEMENT | PD-054,1/3 | -340~2500 mmH2O | 150 | 0~35 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
27 | FE-FA1061-A1 | FE | FA1061-A1 | #1 COAL FEEDER (A) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
28 | FE-FA1061-A2 | FE | FA1061-A2 | #1 COAL FEEDER (A) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
29 | FE-FA1061-A3 | FE | FA1061-A3 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
30 | FE-FA1061-A4 | FE | FA1061-A4 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
31 | FE-FA1061-B1 | FE | FA1061-B1 | #1 COAL FEEDER (B) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
32 | FE-FA1061-B2 | FE | FA1061-B2 | #1 COAL FEEDER (B) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
33 | FE-FA1061-B3 | FE | FA1061-B3 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
34 | FE-FA1061-B4 | FE | FA1061-B4 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
35 | FE-FA1061-C1 | FE | FA1061-C1 | #1 COAL FEEDER (C) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
36 | FE-FA1061-C2 | FE | FA1061-C2 | #1 COAL FEEDER (C) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
37 | FE-FA1061-C3 | FE | FA1061-C3 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
38 | FE-FA1061-C4 | FE | FA1061-C4 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
19 | FE-FA1071 | FE | FA1071 | #1 PRIMARY AIR FAN INLET AIR FLOW ELEMENT | PD-052 | 0 | 66 | - | - | - | - | VENTURI | PACKAGE (PAF) |  | 0 |  | FE
20 | FE-FA1079 | FE | FA1079 | #1 PRIMARY AIR SYSTEM FLOW ELEMENT | PD-052 | -340~2500 mmH2O | 343 | 0~510 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
21 | FE-FA1081 | FE | FA1081 | #1 SECONDARY AIR FAN INLET AIR FLOW ELEMENT | PD-053 | 0 | 66 | - | - | - | - | VENTURI | PACKAGE (SAF) |  | 0 |  | FE
6 | FE-FW1007 | FE | FW1007 | #1 BOILER FEEDWATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~550 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
7 | FE-FW1059 | FE | FW1059 | #1 TURBINE BYPASS DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 100 | 180 | 0~40 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
8 | FE-FW1109 | FE | FW1109 | #1 SUPERHEATER PANEL #1 DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~40 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
9 | FE-FW1119 | FE | FW1119 | #1 SUPERHEATER PANEL #2 DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~40 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
10 | FE-FW1149 | FE | FW1149 | #1 REHEATER INLET DESUPEREHEATEREATING SPRAY WATER FLOW ELEMENT | PD-017 | 100 | 180 | 0~25 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
11 | FE-HD1102 | FE | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN FLOW ELEMENT | PD-018 | 3.6 & Full Vacuum | 150 | 0~27.5 | <125 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
12 | FE-HD1103 | FE | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN FLOW ELEMENT | PD-018 | 3.6 & Full Vacuum | 200 | 0~15 | <1200 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
13 | FE-HD1105 | FE | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN FLOW ELEMENT | PD-018 | 17 & Full Vacuum | 210 | 0~69 | <1250 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
14 | FE-HD1106 | FE | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN FLOW ELEMENT | PD-018 | 47 & Full Vacuum | 260 | 0~45 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
1 | FE-MS1031 | FE | MS1031 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER FLOW ELEMENT | PD-011 | 144 | 550 | 0~500 | <5000 | - |  | FLOW NOZZLE | FHI |  | 0 |  | FE
24 | FG-1401 | FG | 1401 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
25 | FG-1402 | FG | 1402 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
26 | FG-1404 | FG | 1404 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
27 | FG-1405 | FG | 1405 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
28 | FG-1406 | FG | 1406 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
29 | FG-1407 | FG | 1407 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
30 | FG-1408 | FG | 1408 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
31 | FG-1409 | FG | 1409 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
32 | FG-1420 | FG | 1420 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
33 | FG-1422 | FG | 1422 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
1 | FG-CW1140-6 | FG | CW1140-6 | #1 SAMPLING SYSTEM CHILLER UNIT WATER FLOWMETER | PD-044 | - | - | 1~10L/H | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
2 | FG-CW1140-7 | FG | CW1140-7 | #1 SAMPLING SYSTEM COOLING WATER RETURN LINE FLOWMETER | PD-044 | 5 | 40 | 2.5~25L/H | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
34 | FG-FA1009-A1 | FG | FA1009-A1 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE A | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
35 | FG-FA1009-A2 | FG | FA1009-A2 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE B | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
36 | FG-FA1009-B1 | FG | FA1009-B1 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE A | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
37 | FG-FA1009-B2 | FG | FA1009-B2 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE B | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
38 | FG-FA1061-A1 | FG | FA1061-A1 | #1 COAL FEEDER (A) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
39 | FG-FA1061-A2 | FG | FA1061-A2 | #1 COAL FEEDER (A) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
40 | FG-FA1061-A3 | FG | FA1061-A3 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
41 | FG-FA1061-A4 | FG | FA1061-A4 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
42 | FG-FA1061-B1 | FG | FA1061-B1 | #1 COAL FEEDER (B) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
43 | FG-FA1061-B2 | FG | FA1061-B2 | #1 COAL FEEDER (B) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
44 | FG-FA1061-B3 | FG | FA1061-B3 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
45 | FG-FA1061-B4 | FG | FA1061-B4 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
46 | FG-FA1061-C1 | FG | FA1061-C1 | #1 COAL FEEDER (C) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
47 | FG-FA1061-C2 | FG | FA1061-C2 | #1 COAL FEEDER (C) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
48 | FG-FA1061-C3 | FG | FA1061-C3 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
49 | FG-FA1061-C4 | FG | FA1061-C4 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
3 | FG-SP1001 | FG | SP1001 | #1 DEAERATOR UPSTREAM FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
4 | FG-SP1002 | FG | SP1002 | #1 DEAERATOR UPSTREAM FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
5 | FG-SP1003 | FG | SP1003 | #1 DEAERATOR OUTLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
6 | FG-SP1004 | FG | SP1004 | #1 DEAERATOR OUTLET FLOWMETER FOR DISSOLVED OXYGEN SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
7 | FG-SP1005 | FG | SP1005 | #1 DEAERATOR OUTLET FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
8 | FG-SP1006 | FG | SP1006 | #1 MAKE-UP WATER PUMP OUTLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
9 | FG-SP1007 | FG | SP1007 | #1 MAKE-UP WATER PUMP OUTLET FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
10 | FG-SP1008 | FG | SP1008 | #1 MAKE-UP WATER PUMP OUTLET FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
11 | FG-SP1009 | FG | SP1009 | #1 ECONOMIZER INLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
12 | FG-SP1010 | FG | SP1010 | #1 ECONOMIZER INLET FLOWMETER FOR DISSOLVED OXYGEN SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
13 | FG-SP1011 | FG | SP1011 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
14 | FG-SP1012 | FG | SP1012 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
15 | FG-SP1013 | FG | SP1013 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
16 | FG-SP1014 | FG | SP1014 | #1 SATURATED STEAM FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
17 | FG-SP1015 | FG | SP1015 | #1 SATURATED STEAM FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
18 | FG-SP1016 | FG | SP1016 | #1 MAIN STEAM LINE FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
19 | FG-SP1017 | FG | SP1017 | #1 MAIN STEAM LINE FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
20 | FG-SP1018 | FG | SP1018 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR 1st CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
21 | FG-SP1019 | FG | SP1019 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR 2nd CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
22 | FG-SP1020 | FG | SP1020 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR SODIUM ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
23 | FG-SP1021 | FG | SP1021 | #1 MAIN STEAM LINE FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
3 | FS-CW1060-A1 | FS | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
4 | FS-CW1060-A2 | FS | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
5 | FS-CW1060-B1 | FS | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
6 | FS-CW1060-B2 | FS | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
7 | FS-CW1060-C1 | FS | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
8 | FS-CW1060-C2 | FS | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
9 | FS-CW1060-D1 | FS | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
10 | FS-CW1060-D2 | FS | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
2 | FT-CD1115 | FT | CD1115 | #1 LP TURBINE BYPASS SPRAY WATER FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~46 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
3 | FT-CD1120 | FT | CD1120 | #1 CONDENSATE WATER FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
4 | FT-CD1121 | FT | CD1121 | #1 CONDESATE POLISHER SYSTEM INLET FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~200 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
5 | FT-CD1122 | FT | CD1122 | #1 DEAERATOR INLET CONDESATE FLOW TRANSMITTER | PD-016 | 24 | 200 | 0~450 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
1 | FT-CL1061-A | FT | CL1061-A | #1 A-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
2 | FT-CL1061-B | FT | CL1061-B | #1 B-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
3 | FT-CL1061-C | FT | CL1061-C | #1 C-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
4 | FT-DO1043-A | FT | DO1043-A | #1 BURNER(A) DIESEL OIL FLOW TRANSMITTER | PD-022,2/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
50 | FT-DO1043-B | FT | DO1043-B | #1 BURNER(B) DIESEL OIL FLOW TRANSMITTER | PD-022,3/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
96 | FT-DO1043-C | FT | DO1043-C | #1 BURNER(C) DIESEL OIL FLOW TRANSMITTER | PD-022,4/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
142 | FT-DO1043-D | FT | DO1043-D | #1 BURNER(D) DIESEL OIL FLOW TRANSMITTER | PD-022,5/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
16 | FT-FA1043-A | FT | FA1043-A | #1 START-UP BURNER(A) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,2/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
17 | FT-FA1043-B | FT | FA1043-B | #1 START-UP BURNER(B) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,3/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
18 | FT-FA1043-C | FT | FA1043-C | #1 START-UP BURNER(C) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,4/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
19 | FT-FA1043-D | FT | FA1043-D | #1 START-UP BURNER(D) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,5/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
24 | FT-FA1055 | FT | FA1055 | #1 FLUIDIZING AIR BLOWER OUTLET COMMON FLOW TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 150 | 0~35 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
21 | FT-FA1071 | FT | FA1071 | #1 PRIMARY AIR FAN INLET AIR FLOW TRANSMITTER | PD-052 | 0 | 66 | 0~648 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
22 | FT-FA1079 | FT | FA1079 | #1 PRIMARY AIR SYSTEM FLOW TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~510 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
23 | FT-FA1081 | FT | FA1081 | #1 SECONDARY AIR FAN INLET AIR FLOW TRANSMITTER | PD-053 | 0 | 66 | 0~432 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
20 | FT-FG1057-7 | FT | FG1057-7 | #1 STACK FLUE GAS FLOW TRANSMITTER | PD-051 | 33 mmH2O | 200 | 0~886.6 | WET AI 4~20mA | FIELD | DCS | ULTRASONIC | PACKAGE (CEMS) |  | 0 |  | FT
6 | FT-FW1007-1 | FT | FW1007-1 | #1 BOILER FEEDWATER FLOW TRANSMITTER-1 | PD-017 | 230 | 275 | 0~550 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
7 | FT-FW1007-2 | FT | FW1007-2 | #1 BOILER FEEDWATER FLOW TRANSMITTER-2 | PD-017 | 230 | 275 | 0~550 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
8 | FT-FW1059 | FT | FW1059 | #1 TURBINE BYPASS DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 100 | 180 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
9 | FT-FW1109 | FT | FW1109 | #1 SUPERHEATER PANEL #1 DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 230 | 275 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
10 | FT-FW1119 | FT | FW1119 | #1 SUPERHEATER PANEL #2 DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 230 | 275 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
11 | FT-FW1149 | FT | FW1149 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 100 | 180 | 0~25 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
12 | FT-HD1102 | FT | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN FLOW TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 150 | 0~27.5 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
13 | FT-HD1103 | FT | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN FLOW TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 200 | 0~15 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
14 | FT-HD1105 | FT | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN FLOW TRANSMITTER | PD-018 | 16 & Full Vaccum | 210 | 0~69 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
15 | FT-HD1106 | FT | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN FLOW TRANSMITTER | PD-018 | 45 & Full Vaccum | 260 | 0~45 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
1 | FT-MS1031 | FT | MS1031 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER FLOW TRANSMITTER | PD-011 | 144 | 550 | 0~500 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
11 | LCV-CD1104 | LCV | CD1104 | #1 DEAERATOR LEVEL CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
12 | LCV-CD1110 | LCV | CD1110 | #1 CONDENSATE DUMPING VALVE TO RAW WATER PIT LEVEL CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
25 | LCV-HD1101-1 | LCV | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
26 | LCV-HD1101-2 | LCV | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
27 | LCV-HD1102-1 | LCV | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
28 | LCV-HD1102-2 | LCV | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
29 | LCV-HD1103-1 | LCV | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 200 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
30 | LCV-HD1103-2 | LCV | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 200 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
31 | LCV-HD1105-1 | LCV | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE | PD-018 | 16 | 210 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
32 | LCV-HD1105-2 | LCV | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE | PD-018 | 16 & Full Vaccum | 210 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
33 | LCV-HD1106-1 | LCV | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE | PD-018 | 45 | 260 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
34 | LCV-HD1106-2 | LCV | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE | PD-018 | 45 & Full Vaccum | 260 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
13 | LCV-MU1110 | LCV | MU1110 | #1 CONDENER MAKEUP WATER LEVEL CONTROL VALVE | PD-016 | 10 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
1 | LG-0762A | LG | 0762A | HYPO-CHLORINATED DOSING SYSTEM TANK T-0762A LEVEL GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
2 | LG-0762B | LG | 0762B | HYPO-CHLORINATED DOSING SYSTEM TANK T-0762B LEVEL GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
10 | LG-BD1050 | LG | BD1050 | #1 FLASH TANK LEVEL GAUGE | PD-019 | 12.5 | 193 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
11 | LG-BR1001-1 | LG | BR1001-1 | #1 DRUM LEVEL GAUGE | PD-019 | 155.4 | 343 | 0~470 | - | - | - | BI-COLOR | FHI |  | 0 |  | LG
12 | LG-BR1001-2 | LG | BR1001-2 | #1 DRUM LEVEL GAUGE | PD-019 | 155.4 | 343 | 0~470 | - | - | - | BI-COLOR | FHI |  | 0 |  | LG
1 | LG-CD1104 | LG | CD1104 | #1 DEAERATOR STORAGE TANK WATER LEVEL GAUGE | PD-016 | 8 | 170 | 0~2550 | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
2 | LG-CD1110 | LG | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL GAUGE | PD-016 | Full Vaccum & 1.03 | 120 | 0~600 | - | - | - | REFLEX | FHI |  | 0 |  | LG
31 | LG-CH1101 | LG | CH1101 | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE SOLUTION TANK Z-1101 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
32 | LG-CH1102 | LG | CH1102 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1102 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
33 | LG-CH1103 | LG | CH1103 | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE SOLUTION TANK Z-1103 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
34 | LG-CH1104 | LG | CH1104 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1104 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
35 | LG-CH1105 | LG | CH1105 | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE SOLUTION TANK Z-1105 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
36 | LG-CH1106 | LG | CH1106 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1106 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
13 | LG-CW1109 | LG | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL GAUGE | PD-021 | 10 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
14 | LG-DO0701-1 | LG | DO0701-1 | OIL SERVICE TANK LEVEL GAUGE-1 | PD-022,1/5 | 1.5 | 70 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
15 | LG-DO0701-2 | LG | DO0701-2 | OIL SERVICE TANK LEVEL GAUGE-2 | PD-022,1/5 | 1.5 | 70 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
16 | LG-DO0701-3 | LG | DO0701-3 | OIL SERVICE TANK LEVEL GAUGE-3 | PD-022,1/5 | 1.5 | 70 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
17 | LG-DO0701-4 | LG | DO0701-4 | OIL SERVICE TANK LEVEL GAUGE-4 | PD-022,1/5 | 1.5 | 70 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
18 | LG-DO0701-5 | LG | DO0701-5 | OIL SERVICE TANK LEVEL GAUGE-5 | PD-022,1/5 | 1.5 | 70 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
1 | LG-FA1052-1 | LG | FA1052-1 | #1 AIR PRE-HEATER LEVEL GLASS BOTTOM BERATING | - | - | - | - | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
2 | LG-FA1052-2 | LG | FA1052-2 | #1 AIR PRE-HEATER LEVEL GLASS TOP BERATING | - | - | - | - | - | - |  | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
5 | LG-FA1055-A1 | LG | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) OIL LEVEL GAUGE(OIL CUP)-1 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
6 | LG-FA1055-A2 | LG | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) OIL LEVEL GAUGE(OIL CUP)-2 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
7 | LG-FA1055-B1 | LG | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) OIL LEVEL GAUGE(OIL CUP)-1 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
8 | LG-FA1055-B2 | LG | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) OIL LEVEL GAUGE(OIL CUP)-2 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
5 | LG-HD1101 | LG | HD1101 | #1 LOW PRESSURE HEATER NO.1 LEVEL GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
6 | LG-HD1102 | LG | HD1102 | #1 LOW PRESSURE HEATER NO.2 LEVEL GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
7 | LG-HD1103 | LG | HD1103 | #1 LOW PRESSURE HEATER NO.3 LEVEL GAUGE | PD-018 | 3.6 | 200 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
8 | LG-HD1105 | LG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 LEVEL GAUGE | PD-018 | 16 | 210 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
9 | LG-HD1106 | LG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 LEVEL GAUGE | PD-018 | 45 | 260 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
21 | LG-IW0714-1 | LG | IW0714-1 | INDUSTRIAL WATER TANK LEVEL GAUGE-1 | PD-025 | 1.5 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
22 | LG-IW0714-2 | LG | IW0714-2 | INDUSTRIAL WATER TANK LEVEL GAUGE-2 | PD-025 | 1.5 | 65 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
23 | LG-IW0714-3 | LG | IW0714-3 | INDUSTRIAL WATER TANK LEVEL GAUGE-3 | PD-025 | 1.5 | 65 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
24 | LG-IW0714-4 | LG | IW0714-4 | INDUSTRIAL WATER TANK LEVEL GAUGE-4 | PD-025 | 1.5 | 65 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
25 | LG-IW0714-5 | LG | IW0714-5 | INDUSTRIAL WATER TANK LEVEL GAUGE-5 | PD-025 | 1.5 | 65 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
26 | LG-IW0724-1 | LG | IW0724-1 | FIRE WATER TANK LEVEL GAUGE-1 | PD-025 | 1.5 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
27 | LG-IW0724-2 | LG | IW0724-2 | FIRE WATER TANK LEVEL GAUGE-2 | PD-025 | 1.5 | 65 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
28 | LG-IW0724-3 | LG | IW0724-3 | FIRE WATER TANK LEVEL GAUGE-3 | PD-025 | 1.5 | 65 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
29 | LG-IW0724-4 | LG | IW0724-4 | FIRE WATER TANK LEVEL GAUGE-4 | PD-025 | 1.5 | 65 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
30 | LG-IW0724-5 | LG | IW0724-5 | FIRE WATER TANK LEVEL GAUGE-5 | PD-025 | 1.5 | 65 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
3 | LG-LO1115-A | LG | LO1115-A | #1 BFP(A) LUBE OIL LEVEL GAUGE | PD-017 | - | - | 380 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | LG
4 | LG-LO1115-B | LG | LO1115-B | #1 BFP(B) LUBE OIL LEVEL GAUGE | PD-017 | - | - | 380 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | LG
4 | LG-LO1756-2 | LG | LO1756-2 | #1 INDUCED DRAFT FAN OIL LEVEL GAUGE | PD-051 | - | - | - | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
19 | LG-MU0708-A | LG | MU0708-A | DEMINERALIZED WATER TANK A LEVEL GAUGE | PD-024 | 1.5 | 65 | 0~15 M | - | - | - | FLOAT | FHI |  | 0 |  | LG
20 | LG-MU0708-B | LG | MU0708-B | DEMINERALIZED WATER TANK B LEVEL GAUGE | PD-024 | 1.5 | 65 | 0~15 M | - | - | - | FLOAT | FHI |  | 0 |  | LG
4 | LS-CL1061-A3 | LS | CL1061-A3 | #1 A-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
5 | LS-CL1061-A4 | LS | CL1061-A4 | #1 A-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
6 | LS-CL1061-A5 | LS | CL1061-A5 | #1 A-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
7 | LS-CL1061-A6 | LS | CL1061-A6 | #1 A-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
8 | LS-CL1061-B3 | LS | CL1061-B3 | #1 B-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
9 | LS-CL1061-B4 | LS | CL1061-B4 | #1 B-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
10 | LS-CL1061-B5 | LS | CL1061-B5 | #1 B-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
11 | LS-CL1061-B6 | LS | CL1061-B6 | #1 B-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
12 | LS-CL1061-C3 | LS | CL1061-C3 | #1 C-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
13 | LS-CL1061-C4 | LS | CL1061-C4 | #1 C-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
14 | LS-CL1061-C5 | LS | CL1061-C5 | #1 C-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
15 | LS-CL1061-C6 | LS | CL1061-C6 | #1 C-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
1 | LS-CR1001-1 | LS | CR1001-1 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 HIGH LEVEL SWITCH | PD-011 | 45 | 395 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
2 | LS-CR1001-2 | LS | CR1001-2 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 HIGH-HIGH LEVEL SWITCH | PD-011 | 45 | 395 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
30 | LS-FS1410 | LS | FS1410 | #1 FLASH PIPE LEVEL HIGH SWITCH | PD-027 | 3 | 410 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
31 | LS-FS1411 | LS | FS1411 | #1 FLASH PIPE LEVEL LOW SWITCH | PD-027 | 3 | 410 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
6 | LS-FW1115-A | LS | FW1115-A | #1 BFP(A) MOTOR LEAKAGE DETECTOR | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
7 | LS-FW1115-B | LS | FW1115-B | #1 BFP(B) MOTOR LEAKAGE DETECTOR | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
15 | LSH-BR1001-1 | LSH | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
20 | LSH-BR1001-2 | LSH | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
51 | LSH-CH0701 | LSH | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL HIGH SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0 |  | LS
36 | LSH-CH1101 | LSH | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
39 | LSH-CH1103 | LSH | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
42 | LSH-CH1105 | LSH | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
44 | LSH-CL1008-A | LSH | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
46 | LSH-CL1008-B | LSH | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
48 | LSH-CL1008-C | LSH | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
10 | LS-HD1101 | LS | HD1101 | #1 LOW PRESSURE HEATER NO.1 LEVEL SWITCH-3 | PD-018 | Full Vaccum & 3.6 | 150 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
11 | LS-HD1102 | LS | HD1102 | #1 LOW PRESSURE HEATER NO.2 LEVEL SWITCH-3 | PD-018 | Full Vaccum & 3.6 | 150 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
12 | LS-HD1103 | LS | HD1103 | #1 LOW PRESSURE HEATER NO.3 LEVEL SWITCH-3 | PD-018 | 3.6 | 200 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
13 | LS-HD1105 | LS | HD1105 | #1 HIGH PRESSURE HEATER NO.1 LEVEL SWITCH-3 | PD-018 | 16 | 210 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
14 | LS-HD1106 | LS | HD1106 | #1 HIGH PRESSURE HEATER NO.2 LEVEL SWITCH-3 | PD-018 | 45 | 260 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
16 | LSHH-BR1001-1 | LSHH | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (HIGH HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
21 | LSHH-BR1001-2 | LSHH | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (HIGH HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
5 | LSHH-CD1110 | LSHH | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL(HIGH-HIGH) SWITCH | PD-016 | Full Vaccum & 1.03 | 120 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
28 | LS-IW0714 | LS | IW0714 | INDUSTRIAL WATER TANK LEVEL LOW SWITCH | PD-025 | 1.5 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0 |  | LS
29 | LS-IW0724 | LS | IW0724 | FIRE WATER TANK LEVEL LOW SWITCH | PD-025 | 1.5 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0 |  | LS
17 | LSL-BR1001-1 | LSL | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
22 | LSL-BR1001-2 | LSL | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
50 | LSL-CH0701 | LSL | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL LOW SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0 |  | LS
35 | LSL-CH1101 | LSL | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
38 | LSL-CH1103 | LSL | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
41 | LSL-CH1105 | LSL | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
43 | LSL-CL1008-A | LSL | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
45 | LSL-CL1008-B | LSL | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
47 | LSL-CL1008-C | LSL | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
18 | LSLL-BR1001-1 | LSLL | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
19 | LSLL-BR1001-1-NC | LSLL | BR1001-1-NC | #1 DRUM LEVEL SWITCH-1 (NOT LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
23 | LSLL-BR1001-2 | LSLL | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
24 | LSLL-BR1001-2-NC | LSLL | BR1001-2-NC | #1 DRUM LEVEL SWITCH-2 ( NOT LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
3 | LSLL-CD1104-4 | LSLL | CD1104-4 | #1 DEAERATOR STORAGE TANK WATER LEVEL LOW-LOW SWITCH-4 | PD-016 | 8 | 170 | - | DI | FIELD | ARP | FLOAT | FHI |  | 0 |  | LS
4 | LSLL-CD1110 | LSLL | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL(LOW-LOW) SWITCH | PD-016 | Full Vaccum & 1.03 | 120 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
49 | LSLL-CH0701 | LSLL | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0 |  | LS
34 | LSLL-CH1101 | LSLL | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
37 | LSLL-CH1103 | LSLL | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
40 | LSLL-CH1105 | LSLL | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
25 | LSLL-CW1109 | LSLL | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL LOW-LOW SWITCH | PD-021 | 10 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0 |  | LS
3 | LSLL-LO1753 | LSLL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL LEVEL SWITCH | PD-052 | - | - | 270L(<200L) | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
2 | LSL-LO1753 | LSL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL LEVEL SWITCH | PD-052 | - | - | 270L(<240L) | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
8 | LS-LO1115-A | LS | LO1115-A | #1 BFP(A) LUBE OIL LEVEL SWITCH (LOW ALARM) | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
9 | LS-LO1115-B | LS | LO1115-B | #1 BFP(B) LUBE OIL LEVEL SWITCH (LOW ALARM) | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
26 | LS-MU0708-A | LS | MU0708-A | DEMINERALIZED WATER TANK A LEVEL LOW SWITCH | PD-024 | 1.5 | 65 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
27 | LS-MU0708-B | LS | MU0708-B | DEMINERALIZED WATER TANK B LEVEL LOW SWITCH | PD-024 | 1.5 | 65 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
32 | LS-WW0058 | LS | WW0058 | WASTEWATER PIT T-0058 LEVEL SWITCH(HIGH-HIGH, HIGH, LOW, LOW-LOW) | PD-040 | 0.3 | 95 | - | DI | FIELD | LCP | ELECTRODE | FHI |  | 0 |  | LS
33 | LS-WW1127 | LS | WW1127 | #1 TRANSFORMER AREA PIT A LEVEL SWITCH (LO-LO/LO/HI/HI-HI) | PD-040 | 0.25 | 45 |  | DI | FIELD | LCP | ELECTRODE | FHI |  | 0 |  | LS
15 | LT-BR1001-1 | LT | BR1001-1 | #1 DRUM LEVEL -1 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
16 | LT-BR1001-2 | LT | BR1001-2 | #1 DRUM LEVEL -2 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
17 | LT-BR1001-3 | LT | BR1001-3 | #1 DRUM LEVEL -3 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
1 | LT-CD1104-1 | LT | CD1104-1 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-1 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
2 | LT-CD1104-2 | LT | CD1104-2 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-2 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
3 | LT-CD1104-3 | LT | CD1104-3 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-3 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
4 | LT-CD1110 | LT | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL TRANSMITTER | PD-016 | Full Vaccum & 1.03 | 120 | 0~900 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
29 | LT-CL1008-A | LT | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
30 | LT-CL1008-B | LT | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
31 | LT-CL1008-C | LT | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
19 | LT-CW1109 | LT | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL TRANSMITTER | PD-021 | 10 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
20 | LT-DO0701 | LT | DO0701 | OIL SERVICE TANK LEVEL TRANSMITTER | PD-022,1/5 | 1.5 | 70 | 0~8.2 M | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
5 | LT-HD1101-1 | LT | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 LEVEL TRANSMITTER-1 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
6 | LT-HD1101-2 | LT | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 LEVEL TRANSMITTER-2 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
7 | LT-HD1102-1 | LT | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 LEVEL TRANSMITTER-1 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
8 | LT-HD1102-2 | LT | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 LEVEL TRANSMITTER-2 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
9 | LT-HD1103-1 | LT | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 LEVEL TRANSMITTER-1 | PD-018 | 3.6 | 210 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
10 | LT-HD1103-2 | LT | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 LEVEL TRANSMITTER-2 | PD-018 | 3.6 | 210 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
11 | LT-HD1105-1 | LT | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 LEVEL TRANSMITTER-1 | PD-018 | 16 | 440 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
12 | LT-HD1105-2 | LT | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 LEVEL TRANSMITTER-2 | PD-018 | 16 | 440 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
13 | LT-HD1106-1 | LT | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 LEVEL TRANSMITTER-1 | PD-018 | 45 | 395 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
14 | LT-HD1106-2 | LT | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 LEVEL TRANSMITTER-2 | PD-018 | 45 | 395 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
23 | LT-IW0113 | LT | IW0113 | TURBINE BUILDING PLUMBING WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
24 | LT-IW0714 | LT | IW0714 | INDUSTRIAL WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~8.2 M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
25 | LT-IW0724 | LT | IW0724 | FIRE WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~8.2 M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
21 | LT-MU0708-A | LT | MU0708-A | DEMINERALIZED WATER TANK A LEVEL TRANSMITTER | PD-024 | 1.5 | 65 | 0~15M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
22 | LT-MU0708-B | LT | MU0708-B | DEMINERALIZED WATER TANK B LEVEL TRANSMITTER | PD-024 | 1.5 | 65 | 0~15M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
26 | LT-PW0114 | LT | PW0114 | TURBINE BUILDING POTABLE WATER TANK LEVEL TRANSMITTER | PD-026 | 3 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
27 | LT-PW0721 | LT | PW0721 | WATER TREATMENT PLANT CONTROL BUILDING POTABLE WATER TANK LEVEL TRANSMITTER | PD-026 | 3 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
28 | LT-RW0717 | LT | RW0717 | RAW WATER PIT LEVEL TRANSMITTER | PD-045 | 1 | 45 | 0.5~5M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
18 | LT-SW1501 | LT | SW1501 | #1 SEAWATER PUMP INLET LEVEL TRANSMITTER | PD-020 | 1 | 65 | 0.5~15M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
1 | MCV-FA1005 | MCV | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
2 | MCV-FA1006 | MCV | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
3 | MCV-FA1007 | MCV | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
4 | MCV-FA1008 | MCV | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
5 | MCV-FA1009 | MCV | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
6 | MCV-FA1010 | MCV | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
7 | MCV-FA1011 | MCV | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
8 | MCV-FA1012 | MCV | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
9 | MCV-FA1013 | MCV | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
10 | MCV-FA1014 | MCV | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
11 | MCV-FA1015 | MCV | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
12 | MCV-FA1016 | MCV | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
13 | MCV-FA1017 | MCV | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
14 | MCV-FA1018 | MCV | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
15 | MCV-FA1019 | MCV | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
16 | MCV-FA1020 | MCV | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
17 | MCV-FA1021 | MCV | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
18 | MCV-FA1022 | MCV | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
19 | MCV-FA1023 | MCV | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
20 | MCV-FA1024 | MCV | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
21 | MCV-FA1025 | MCV | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
22 | MCV-FA1026 | MCV | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
5 | MCV-FA1043-A | MCV | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,2/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
51 | MCV-FA1043-B | MCV | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,3/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
97 | MCV-FA1043-C | MCV | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,4/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
143 | MCV-FA1043-D | MCV | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,5/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
1 | MCV-FA1053-1 | MCV | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV | PD-052 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
23 | MCV-FA1054-1 | MCV | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
22 | MV-AS1391 | MV | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV | PD-014 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
23 | MV-AS1392 | MV | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
24 | MV-AS1393 | MV | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV | PD-014 | 13 | 300 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
1 | MV-AS1394 | MV | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV | PD-011 | 13 | 300 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
25 | MV-AS1395 | MV | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
26 | MV-AS1396 | MV | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
48 | MV-AV1391 | MV | AV1391 | #1 CONDENSER VACUUM BREAKER MOV | PD-027 | 1.5 | 120 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
38 | MV-BD1001 | MV | BD1001 | #1 BOILER MASS BLOWDOWN MOV | PD-019 | 155.4 | 343 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
39 | MV-BD1002 | MV | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV | PD-019 | 155.4 | 343 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
40 | MV-BR1391 | MV | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV | PD-019 | 153.5 | 440 | - | DO | DCS | FIELD | DC TYPE | FHI |  | 0 |  | MV
28 | MV-CD1001 | MV | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
29 | MV-CD1002 | MV | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV | PD-016 | 24 | 150 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
30 | MV-CD1003 | MV | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV | PD-016 | 24 | 150 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
31 | MV-CD1007 | MV | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
32 | MV-CD1008 | MV | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
34 | MV-FW1001 | MV | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
35 | MV-FW1002 | MV | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
36 | MV-FW1391 | MV | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
37 | MV-FW1392 | MV | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
4 | MV-HR1391 | MV | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV | PD-012 | 45 | 550 | - | DO | DCS | FIELD | DC TYPE | FHI |  | 0 |  | MV
47 | MV-IW0391 | MV | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV | PD-025 | 1.5 | 65 | - | DO | DCS | FIELD |  | FHI | NEW ADDED | 0 |  | MV
2 | MV-MS1391 | MV | MS1391 | #1 MAIN STEAM SHUT-OFF MOV | PD-011 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
3 | MV-MS1392 | MV | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV | PD-011 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
33 | MV-MU1001 | MV | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV | PD-016 | 10 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
27 | MV-SB1001 | MV | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV | PD-015 | 153.5 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
41 | MV-SW1001 | MV | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | MV
42 | MV-SW1002 | MV | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV | PD-020 | 7 | 50 | - | DO | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | MV
43 | MV-SW1003 | MV | SW1003 | #1 BALL VESSEL T-1116 INLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
44 | MV-SW1004 | MV | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
45 | MV-SW1005 | MV | SW1005 | #1 BALL VESSEL T-1115 INLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
46 | MV-SW1006 | MV | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
5 | MV-TS1001 | MV | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV | PD-013 | 45 | 395 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
6 | MV-TS1002 | MV | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
7 | MV-TS1003 | MV | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
8 | MV-TS1004 | MV | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
9 | MV-TS1005 | MV | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
10 | MV-TS1389 | MV | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV(HEATER SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
11 | MV-TS1390 | MV | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV(HEATER SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
12 | MV-TS1391 | MV | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV(TURBINE SIDE) | PD-013 | 45 | 395 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
13 | MV-TS1392 | MV | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV(TURBINE SIDE) | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
14 | MV-TS1393 | MV | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV(TURBINE SIDE) | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
15 | MV-TS1394 | MV | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV(TURBINE SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
16 | MV-TS1395 | MV | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV(TURBINE SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
17 | MV-TS1396 | MV | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV(HEATER SIDE) | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
18 | MV-TS1397 | MV | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV(HEATER SIDE) | PD-013 | 45 | 395 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
19 | MV-TS1398 | MV | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV(DEAERATORR SIDE) | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
20 | MV-TS1399 | MV | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
21 | MV-TS1400 | MV | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV | PD-013 | 1.5 | 120 | - | DO | DCS | FIELD |  | FHI | NEW ADDED | 0 |  | MV
5 | PCD-FG1056-1 | PCD | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE CONTROL DAMPER | PD-051 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
4 | PCV-AS1010 | PCV | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE | PD-014 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
5 | PCV-AS1020-1 | PCV | AS1020-1 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE (LOW LOAD) | PD-014 | 45 | 395 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
6 | PCV-AS1020-2 | PCV | AS1020-2 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE (HIGH LOAD) | PD-014 | 45 | 395 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
7 | PCV-AS1030 | PCV | AS1030 | #1 DEAERATOR PEGGING STEAM CONTROL VALVE | PD-014 | 13 | 410 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
37 | PCV-DO0002 | PCV | DO0002 | DIESEL OIL SYSTEM PRESSURE CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
38 | PCV-DO1009 | PCV | DO1009 | #1 DIESEL OIL RETURN PRESSURE CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
3 | PCV-HR1010 | PCV | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE | PD-012 | 45 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
1 | PCV-MS1001 | PCV | MS1001 | #1 MAIN STEAM BLOW OFF VALVE | PD-011 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
2 | PCV-MS1020 | PCV | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE | PD-011 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
8 | PCV-SB1053 | PCV | SB1053 | #1 SOOTBLOWING STEAM PRESSURE CONTROL VALVE | PD-015 | 153.5 | 440 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
3 | PG-0761 | PG | 0761 | HYPO-CHLORINATED DOSING SYSTEM TRANSFER PUMP P-0761 DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
5 | PG-0762A | PG | 0762A | HYPO-CHLORINATED DOSING SYSTEM NaOCL DOSING PUMP P-0762A DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
6 | PG-0762B | PG | 0762B | HYPO-CHLORINATED DOSING SYSTEM NaOCL DOSING PUMP P-0762B DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
4 | PG-0766 | PG | 0766 | HYPO-CHLORINATED DOSING PIPE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
2 | PG-AS1006 | PG | AS1006 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE (START-UP) | PD-014 | 11 | 280 | 0~15 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
3 | PG-AS1007 | PG | AS1007 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-1 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
4 | PG-AS1008 | PG | AS1008 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-2 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
5 | PG-AS1009 | PG | AS1009 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-3 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
6 | PG-AS1011 | PG | AS1011 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-4 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
7 | PG-AS1012 | PG | AS1012 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-5 | PD-014 | Full Vaccum & 0 | 350 | -1~0 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
8 | PG-AS1013 | PG | AS1013 | #1 STEAM JET AIR EJECTOR CONDENSER PRESSURE GAUGE-1 | PD-014 | Full Vaccum & 0 | 350 | -1~0 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
9 | PG-AS1014 | PG | AS1014 | #1 STEAM JET AIR EJECTOR CONDENSER PRESSURE GAUGE-2 | PD-014 | 0.055Kg/c㎡A | 30.2 | -1~1 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
53 | PG-BD1050 | PG | BD1050 | #1 FLASH TANK PRESSURE GAUGE | PD-019 | 12.5 | 200 | 0~15 | - | - | - | BOURDON | FHI |  | 0 |  | PG
54 | PG-BR1001 | PG | BR1001 | #1 DRUM PRESSURE GAUGE | PD-019 | 155 | 343 | 0~200 | - | - | - | BOURDON | FHI |  | 0 |  | PG
11 | PG-CD1101-1 | PG | CD1101-1 | #1 LOW PRESSURE HEATER NO.1 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
12 | PG-CD1101-2 | PG | CD1101-2 | #1 LOW PRESSURE HEATER NO.1 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
13 | PG-CD1102-1 | PG | CD1102-1 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
14 | PG-CD1102-2 | PG | CD1102-2 | #1 LOW PRESSURE HEATER NO.2 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
15 | PG-CD1103-1 | PG | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
16 | PG-CD1103-2 | PG | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 200 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
17 | PG-CD1104 | PG | CD1104 | #1 DEAERATOR PRESSURE GAUGE | PD-016 | 8 | 380 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
18 | PG-CD1110 | PG | CD1110 | #1 CONDENSER PRESSURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
19 | PG-CD1116-A1 | PG | CD1116-A1 | #1 CONDENSATE PUMP A SUCTION PRESSURE GAUGE | PD-016 | 3.5 | 65 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
20 | PG-CD1116-A2 | PG | CD1116-A2 | #1 CONDENSATE PUMP A DISCHARGE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
21 | PG-CD1116-B1 | PG | CD1116-B1 | #1 CONDENSATE PUMP B SUCTION PRESSURE GAUGE | PD-016 | 3.5 | 65 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
22 | PG-CD1116-B2 | PG | CD1116-B2 | #1 CONDENSATE PUMP B DISCHARGE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
23 | PG-CD1117 | PG | CD1117 | #1 CONDENSATE WATER PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
131 | PG-CD1716A | PG | CD1716A | #1 CONDENSATE BOOSTER PUMP P-1716A DISCHARGE PRESSURE GAUGE | PD-047 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
132 | PG-CD1716B | PG | CD1716B | #1 CONDENSATE BOOSTER PUMP P-1716B DISCHARGE PRESSURE GAUGE | PD-047 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI | NEW ADDED | 0 |  | PG
111 | PG-CH1107A | PG | CH1107A | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE DOSING PUMP Z-1107A DISCHARGE PRESSURE GAUGE | PD-042 | 184.62 | 35 | 0~250 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
112 | PG-CH1107B | PG | CH1107B | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE DOSING PUMP Z-1107B DISCHARGE PRESSURE GAUGE | PD-042 | 184.62 | 35 | 0~250 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
113 | PG-CH1108A | PG | CH1108A | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE DOSING PUMP Z-1108A DISCHARGE PRESSURE GAUGE | PD-042 | 18.36 | 35 | 0~40 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
114 | PG-CH1108B | PG | CH1108B | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE DOSING PUMP Z-1108B DISCHARGE PRESSURE GAUGE | PD-042 | 18.36 | 35 | 0~40 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
115 | PG-CH1109A | PG | CH1109A | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE DOSING PUMP Z-1109A DISCHARGE PRESSURE GAUGE | PD-042 | 12.24 | 35 | 0~20 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
116 | PG-CH1109B | PG | CH1109B | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE DOSING PUMP Z-1109B DISCHARGE PRESSURE GAUGE | PD-042 | 12.24 | 35 | 0~20 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
11 | PG-CW1060-A | PG | CW1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
12 | PG-CW1060-A1 | PG | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
13 | PG-CW1060-A2 | PG | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
14 | PG-CW1060-B | PG | CW1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
15 | PG-CW1060-B1 | PG | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
16 | PG-CW1060-B2 | PG | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
17 | PG-CW1060-C | PG | CW1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
18 | PG-CW1060-C1 | PG | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
19 | PG-CW1060-C2 | PG | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
20 | PG-CW1060-D | PG | CW1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
21 | PG-CW1060-D1 | PG | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
22 | PG-CW1060-D2 | PG | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
79 | PG-CW1108-A | PG | CW1108-A | #1 AUXILIARY COOLING WATER PUMP A DISCHARGE PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
80 | PG-CW1108-B | PG | CW1108-B | #1 AUXILIARY COOLING WATER PUMP B DISCHARGE PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
117 | PG-CW1140-1 | PG | CW1140-1 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY PRESSURE GAUGE UPSTREAM Y-STRAINER | PD-044 | 5 | 40 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
118 | PG-CW1140-2 | PG | CW1140-2 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY PRESSURE GAUGE DOWWNSTREAM Y-STRAINER | PD-044 | 5 | 40 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
119 | PG-CW1140-4 | PG | CW1140-4 | #1 SAMPLING SYSTEM CHILLER UNIT COOLING WATER SUPPLY PRESSURE GAUGE UPSTREAM Y-STRAINER | PD-044 | 0.5 | 30 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
120 | PG-CW1140-5 | PG | CW1140-5 | #1 SAMPLING SYSTEM CHILLER UNIT COOLING WATER SUPPLY PRESSURE GAUGE DOWNSTREAM Y-STRAINER | PD-044 | 0.5 | 30 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
81 | PG-CW1151 | PG | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK OUTLET PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
82 | PG-CW1157-A | PG | CW1157-A | #1 AUXILIARY COOLING WATER PUMP (A) SUCTION PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
83 | PG-CW1157-B | PG | CW1157-B | #1 AUXILIARY COOLING WATER PUMP (B) SUCTION PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
84 | PG-DO0004 | PG | DO0004 | DIESEL OIL PUMP COMMON DISCHARGE PRESSURE GAUGE | PD-022,1/5 | 25 | 70 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
85 | PG-DO1007 | PG | DO1007 | #1 DIESEL OIL RETURN PRESSURE GAUGE | PD-022,1/5 | 25 | 70 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
6 | PG-DO1043-A | PG | DO1043-A | #1 BURNER(A) DIESEL OIL PRESSURE GAUGE | PD-022,2/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
7 | PG-DO1043-A2 | PG | DO1043-A2 | #1 BURNER(A) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,2/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
52 | PG-DO1043-B | PG | DO1043-B | #1 BURNER(B) DIESEL OIL PRESSURE GAUGE | PD-022,3/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
53 | PG-DO1043-B2 | PG | DO1043-B2 | #1 BURNER(B) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,3/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
98 | PG-DO1043-C | PG | DO1043-C | #1 BURNER(C) DIESEL OIL PRESSURE GAUGE | PD-022,4/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
99 | PG-DO1043-C2 | PG | DO1043-C2 | #1 BURNER(C) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,4/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
144 | PG-DO1043-D | PG | DO1043-D | #1 BURNER(D) DIESEL OIL PRESSURE GAUGE | PD-022,5/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
145 | PG-DO1043-D2 | PG | DO1043-D2 | #1 BURNER(D) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,5/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
93 | PG-DW0858-A | PG | DW0858-A | REGENERATION WATER PUMP P-0858A DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
94 | PG-DW0858-B | PG | DW0858-B | REGENERATION WATER PUMP P-0858B DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
95 | PG-DW0858-C | PG | DW0858-C | REGENERATION WATER PUMP P-0858C DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
8 | PG-FA1043-A | PG | FA1043-A | #1 BURNER(A) AIR PRESSURE GAUGE | PD-022,2/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
54 | PG-FA1043-B | PG | FA1043-B | #1 BURNER(B) AIR PRESSURE GAUGE | PD-022,3/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
100 | PG-FA1043-C | PG | FA1043-C | #1 BURNER(C) AIR PRESSURE GAUGE | PD-022,4/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
146 | PG-FA1043-D | PG | FA1043-D | #1 BURNER(D) AIR PRESSURE GAUGE | PD-022,5/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
133 | PG-FA1055-A | PG | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET PRESSURE GAUGE | PD-054,1/3 | 8700 mmH2O | 150 | 0~10000 mmH2O | - | - | - | DIAPHRAGM | FHI |  | 0 |  | PG
9 | PG-FA1055-A | PG | FA1055-A | #1 FLUIDIZING AIR BLOWER(A) PRESSURE GAUGE | PD-054 | - | - | 0~1Kg/c㎡G | - | - | - | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
134 | PG-FA1055-B | PG | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET PRESSURE GAUGE | PD-054,1/3 | 8700 mmH2O | 150 | 0~10000 mmH2O | - | - | - | DIAPHRAGM | FHI |  | 0 |  | PG
10 | PG-FA1055-B | PG | FA1055-B | #1 FLUIDIZING AIR BLOWER(B) PRESSURE GAUGE | PD-054 | - | - | 0~1Kg/c㎡G | - | - | - | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
24 | PG-FW1105-1 | PG | FW1105-1 | #1 HIGH PRESSURE HEATER NO.1 INLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 180 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
25 | PG-FW1105-2 | PG | FW1105-2 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 220 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
26 | PG-FW1106-1 | PG | FW1106-1 | #1 HIGH PRESSURE HEATER NO.2 INLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 220 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
27 | PG-FW1106-2 | PG | FW1106-2 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 275 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
28 | PG-FW1115-A1 | PG | FW1115-A1 | #1 BFP(A) DISCHAEGE PRESSURE GAUGE | PD-017 | - | - | 0~250 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
29 | PG-FW1115-A2 | PG | FW1115-A2 | #1 BFP(A) BLEED OFF PRESSURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
30 | PG-FW1115-A3 | PG | FW1115-A3 | #1 BFP(A) SUCTION PRESSURE GAUGE | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
31 | PG-FW1115-A4 | PG | FW1115-A4 | #1 BFP(A) BALANCE LINE PRESSURE GAUGE | PD-017 | - | - | 0~25 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
32 | PG-FW1115-A5 | PG | FW1115-A5 | #1 BFP(A) PUMP DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
33 | PG-FW1115-A6 | PG | FW1115-A6 | #1 BFP(A) PUMP NON DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
34 | PG-FW1115-B1 | PG | FW1115-B1 | #1 BFP(B) DISCHAEGE PRESSURE GAUGE | PD-017 | - | - | 0~250 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
35 | PG-FW1115-B2 | PG | FW1115-B2 | #1 BFP(B) BLEED OFF PRESSURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
36 | PG-FW1115-B3 | PG | FW1115-B3 | #1 BFP(B) SUCTION PRESSURE GAUGE | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
37 | PG-FW1115-B4 | PG | FW1115-B4 | #1 BFP(B) BALANCE LINE PRESSURE GAUGE | PD-017 | - | - | 0~25 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
38 | PG-FW1115-B5 | PG | FW1115-B5 | #1 BFP(B) PUMP DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
39 | PG-FW1115-B6 | PG | FW1115-B6 | #1 BFP(B) PUMP NON DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
44 | PG-HD1101 | PG | HD1101 | #1 LOW PRESSURE HEATER NO.1 STEAM PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
45 | PG-HD1102 | PG | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
46 | PG-HD1102-1 | PG | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 STEAM PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
47 | PG-HD1103 | PG | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 200 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
48 | PG-HD1103-1 | PG | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 STEAM PRESSURE GAUGE | PD-018 | 3.6 | 210 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
49 | PG-HD1105 | PG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN PRESSURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
50 | PG-HD1105-1 | PG | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 STEAM PRESSURE GAUGE | PD-018 | 16 | 440 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
51 | PG-HD1106 | PG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN PRESSURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | 0~50 | - | - | - | BOURDON | FHI |  | 0 |  | PG
52 | PG-HD1106-1 | PG | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 STEAM PRESSURE GAUGE | PD-018 | 45 | 395 | 0~50 | - | - | - | BOURDON | FHI |  | 0 |  | PG
91 | PG-IA1064-A | PG | IA1064-A | #1 AIR BUFFER TANK OF BIASING DAMPER A PRESSURE GAUGE | PD-023,5/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
92 | PG-IA1064-B | PG | IA1064-B | #1 AIR BUFFER TANK OF BIASING DAMPER B PRESSURE GAUGE | PD-023,5/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
90 | PG-IA1128 | PG | IA1128 | #1 AIR BUFFER TANK OF TURNING GEAR PRESSURE GAUGE | PD-023,4/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
107 | PG-IW0052 | PG | IW0052 | INDUSTRIAL WATER FOR WASTE WATER PUMP 0050A PRESSURE GAUGE | PD-040 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
108 | PG-IW0053 | PG | IW0053 | INDUSTRIAL WATER FOR WASTE WATER PUMP 0050B PRESSURE GAUGE | PD-040 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
99 | PG-IW0715-A | PG | IW0715-A | INDUSTRIAL WATER PUMP A DISCHARGE PRESSURE GAUGE | PD-025 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
100 | PG-IW0715-B | PG | IW0715-B | INDUSTRIAL WATER PUMP B DISCHARGE PRESSURE GAUGE | PD-025 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
101 | PG-IW0808-A | PG | IW0808-A | ACTIVATED CARBON FILTER FEED PUMP P-0808A DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
102 | PG-IW0808-B | PG | IW0808-B | ACTIVATED CARBON FILTER FEED PUMP P-0808B DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
103 | PG-IW0809-A | PG | IW0809-A | ACTIVATED CARBON FILTER BACKWASH PUMP P-0809A DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
104 | PG-IW0809-B | PG | IW0809-B | ACTIVATED CARBON FILTER BACKWASH PUMP P-0809B DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
105 | PG-IW0895-A | PG | IW0895-A | UTILITY WATER PUMP P-0895A DISCHARGE PRESSURE GAUGE | PD-025 | 4 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
106 | PG-IW0895-B | PG | IW0895-B | UTILITY WATER PUMP P-0895B DISCHARGE PRESSURE GAUGE | PD-025 | 4 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
40 | PG-LO1115-A1 | PG | LO1115-A1 | #1 BFP(A) LUBE OIL PRESSURE GAUGE-1 | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
41 | PG-LO1115-A2 | PG | LO1115-A2 | #1 BFP(A) LUBE OIL PRESSURE GAUGE-2 | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
42 | PG-LO1115-B1 | PG | LO1115-B1 | #1 BFP(B) LUBE OIL PRESSURE GAUGE-1 | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
43 | PG-LO1115-B2 | PG | LO1115-B2 | #1 BFP(B) LUBE OIL PRESSURE GAUGE-2 | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
4 | PG-LO1753-1 | PG | LO1753-1 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-1 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
5 | PG-LO1753-2 | PG | LO1753-2 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-2 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
6 | PG-LO1753-3 | PG | LO1753-3 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-3 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
7 | PG-LO1753-4 | PG | LO1753-4 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-4 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
8 | PG-LO1753-5 | PG | LO1753-5 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-5 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
9 | PG-LO1753-6 | PG | LO1753-6 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-6 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
6 | PG-LO1756-1 | PG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL PRESSURE GAUGE AT UPSTREAM OF COUPLING | PD-051 | - | - | 0~4.08 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
7 | PG-LO1756-2 | PG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL PRESSURE GAUGE AT DOWNSTREAM OF LUBE OIL ORIFICE | PD-051 | - | - | 0~1.1 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
1 | PG-MS1003 | PG | MS1003 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER PRESSURE GAUGE | PD-011 | 144 | 550 | 0~200 | - | - | - | BOURDON | FHI |  | 0 |  | PG
96 | PG-MU0709-A | PG | MU0709-A | MAKE-UP PUMP A DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
97 | PG-MU0709-B | PG | MU0709-B | MAKE-UP PUMP B DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
98 | PG-MU0709-C | PG | MU0709-C | MAKE-UP PUMP C DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
86 | PG-PA0705A | PG | PA0705A | #1 PLANT AIR TANK T-0705A PRESSURE GAUGE | PD-023,1/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
87 | PG-PA0705B | PG | PA0705B | #1 PLANT AIR TANK T-0705B PRESSURE GAUGE | PD-023,1/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
88 | PG-PA0706A | PG | PA0706A | #1 INSTRUMENT AIR TANK T-0706A PRESSURE GAUGE | PD-023,2/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
89 | PG-PA0706B | PG | PA0706B | #1 INSTRUMENT AIR TANK T-0706B PRESSURE GAUGE | PD-023,2/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
9 | PG-PA1043-A1 | PG | PA1043-A1 | #1 BURNER(A) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,2/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
10 | PG-PA1043-A2 | PG | PA1043-A2 | #1 BURNER(A) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,2/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
55 | PG-PA1043-B1 | PG | PA1043-B1 | #1 BURNER(B) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,3/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
56 | PG-PA1043-B2 | PG | PA1043-B2 | #1 BURNER(B) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,3/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
101 | PG-PA1043-C1 | PG | PA1043-C1 | #1 BURNER(C) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,4/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
102 | PG-PA1043-C2 | PG | PA1043-C2 | #1 BURNER(C) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,4/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
147 | PG-PA1043-D1 | PG | PA1043-D1 | #1 BURNER(D) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,5/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
148 | PG-PA1043-D2 | PG | PA1043-D2 | #1 BURNER(D) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,5/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
3 | PG-PA1052 | PG | PA1052 | #1 AIR PRE-HEATER AIR MOTOR SUPPLY PRESSURE GAUGE | - | - | - | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (AIR PRE HEATER) | NEW ADDED | 1 |  | AIR PREHEATER
23 | PG-PA1060-A | PG | PA1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
24 | PG-PA1060-B | PG | PA1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
25 | PG-PA1060-C | PG | PA1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
26 | PG-PA1060-C | PG | PA1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060D PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
1 | PG-PA1066A~I | PG | PA1066A~I | #1 COAL BUNKER A (T-1008A) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
2 | PG-PA1067A~I | PG | PA1067A~I | #1 COAL BUNKER B (T-1008B) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
3 | PG-PA1068A~I | PG | PA1068A~I | #1 COAL BUNKER C (T-1008C) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
129 | PG-RW0862-A | PG | RW0862-A | RAW WATER FEED PUMP P-0862A DISCHARGE PRESSURE GAUGE | PD-045 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
130 | PG-RW0862-B | PG | RW0862-B | RAW WATER FEED PUMP P-0862B DISCHARGE PRESSURE GAUGE | PD-045 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
10 | PG-SB1051 | PG | SB1051 | #1 SOOTBLOWING HEADER STEAM PRESSURE GAUGE | PD-015 | 30 | 360 | 0~50 | - | - | - | BOURDON | FHI |  | 0 |  | PG
121 | PG-SP1001 | PG | SP1001 | #1 DEAERATOR UPSTREAM PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
122 | PG-SP1002 | PG | SP1002 | #1 DEAERATOR OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
123 | PG-SP1003 | PG | SP1003 | #1 MAKE-UP WATER PUMP OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
124 | PG-SP1004 | PG | SP1004 | #1 ECONOMIZER INLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
125 | PG-SP1005 | PG | SP1005 | #1 DRUM WATER (BLOW DOWN) PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
126 | PG-SP1006 | PG | SP1006 | #1 SATURATED STEAM PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
127 | PG-SP1007 | PG | SP1007 | #1 MAIN STEAM LINE PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
128 | PG-SP1008 | PG | SP1008 | #1 CONDENSATE PUMP OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
55 | PG-SW1107-A1 | PG | SW1107-A1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
56 | PG-SW1107-A2 | PG | SW1107-A2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
57 | PG-SW1107-B1 | PG | SW1107-B1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
58 | PG-SW1107-B2 | PG | SW1107-B2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
59 | PG-SW1107-C1 | PG | SW1107-C1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
60 | PG-SW1107-C2 | PG | SW1107-C2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
61 | PG-SW1110-A1 | PG | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
62 | PG-SW1110-A2 | PG | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
63 | PG-SW1110-B1 | PG | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
64 | PG-SW1110-B2 | PG | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
65 | PG-SW1113-1 | PG | SW1113-1 | #1 BALL RECIRCULATING PUMP M-1113 SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~2.5 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
66 | PG-SW1113-2 | PG | SW1113-2 | #1 BALL RECIRCULATING PUMP M-1113 DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~4 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
67 | PG-SW1114-1 | PG | SW1114-1 | #1 BALL RECIRCULATING PUMP M-1114 SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~2.5 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
68 | PG-SW1114-2 | PG | SW1114-2 | #1 BALL RECIRCULATING PUMP M-1114 DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~4 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
69 | PG-SW1501-A | PG | SW1501-A | #1 SEAWATER PUMP (A) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
70 | PG-SW1501-B | PG | SW1501-B | #1 SEAWATER PUMP (B) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
71 | PG-SW1501-C | PG | SW1501-C | #1 SEAWATER PUMP (C) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
72 | PG-SW1503-A1 | PG | SW1503-A1 | #1 SEAWATER BOOSTER PUMP A SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
73 | PG-SW1503-A2 | PG | SW1503-A2 | #1 SEAWATER BOOSTER PUMP A DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
74 | PG-SW1503-B1 | PG | SW1503-B1 | #1 SEAWATER BOOSTER PUMP B SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
75 | PG-SW1503-B2 | PG | SW1503-B2 | #1 SEAWATER BOOSTER PUMP B DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
76 | PG-SW1503-C1 | PG | SW1503-C1 | #1 SEAWATER BOOSTER PUMP C SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
77 | PG-SW1503-C2 | PG | SW1503-C2 | #1 SEAWATER BOOSTER PUMP C DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
78 | PG-SW1552 | PG | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
109 | PG-WW0058-A | PG | WW0058-A | WASTEWATER PUMP P-0058A DISCHARGE PRESSURE GAUGE | PD-040 | 7 | 90 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
110 | PG-WW0058-B | PG | WW0058-B | WASTEWATER PUMP P-0058B DISCHARGE PRESSURE GAUGE | PD-040 | 7 | 90 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
11 | PRV-PA1043-A | PRV | PA1043-A | #1 BURNER(A) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,2/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
12 | PRV-PA1043-A1 | PRV | PA1043-A1 | #1 BURNER(A) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,2/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
57 | PRV-PA1043-B | PRV | PA1043-B | #1 BURNER(B) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,3/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
58 | PRV-PA1043-B1 | PRV | PA1043-B1 | #1 BURNER(B) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,3/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
103 | PRV-PA1043-C | PRV | PA1043-C | #1 BURNER(C) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,4/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
104 | PRV-PA1043-C1 | PRV | PA1043-C1 | #1 BURNER(C) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,4/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
149 | PRV-PA1043-D | PRV | PA1043-D | #1 BURNER(D) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,5/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
150 | PRV-PA1043-D1 | PRV | PA1043-D1 | #1 BURNER(D) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,5/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
1 | PS-CD1110-1 | PS | CD1110-1 | #1 CONDENSER PRESSURE SWITCH-1 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
2 | PS-CD1110-2 | PS | CD1110-2 | #1 CONDENSER PRESSURE SWITCH-2 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
3 | PS-CD1110-3 | PS | CD1110-3 | #1 CONDENSER PRESSURE SWITCH-3 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
4 | PS-CD1117 | PS | CD1117 | #1 CONDENSATE WATER PRESSURE LOW SWITCH | PD-016 | 24 | 65 | 15.5 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
13 | PSH-DO1043-A1 | PSH | DO1043-A1 | #1 BURNER(A) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,2/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
59 | PSH-DO1043-B1 | PSH | DO1043-B1 | #1 BURNER(B) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,3/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
105 | PSH-DO1043-C1 | PSH | DO1043-C1 | #1 BURNER(C) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,4/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
151 | PSH-DO1043-D1 | PSH | DO1043-D1 | #1 BURNER(D) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,5/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
14 | PSHH-FG1085 | PSHH | FG1085 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
15 | PSHH-FG1085-NC | PSHH | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
16 | PSHH-FG1086 | PSHH | FG1086 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
17 | PSHH-FG1086-NC | PSHH | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
18 | PSHH-FG1087 | PSHH | FG1087 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
19 | PSHH-FG1087-NC | PSHH | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
20 | PSHHH-FG1085 | PSHHH | FG1085 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
21 | PSHHH-FG1085-NC | PSHHH | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
22 | PSHHH-FG1086 | PSHHH | FG1086 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
23 | PSHHH-FG1086-NC | PSHHH | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
24 | PSHHH-FG1087 | PSHHH | FG1087 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
25 | PSHHH-FG1087-NC | PSHHH | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
16 | PS-IA1061-A1 | PS | IA1061-A1 | #1 COAL FEEDER A INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
17 | PS-IA1061-A1 | PS | IA1061-A1 | #1 A-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
18 | PS-IA1061-A2 | PS | IA1061-A2 | #1 COAL FEEDER A INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
19 | PS-IA1061-A2 | PS | IA1061-A2 | #1 A-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
20 | PS-IA1061-B1 | PS | IA1061-B1 | #1 COAL FEEDER B INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
21 | PS-IA1061-B1 | PS | IA1061-B1 | #1 B-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
22 | PS-IA1061-B2 | PS | IA1061-B2 | #1 COAL FEEDER B INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
23 | PS-IA1061-B2 | PS | IA1061-B2 | #1 B-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
24 | PS-IA1061-C1 | PS | IA1061-C1 | #1 COAL FEEDER C INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
25 | PS-IA1061-C1 | PS | IA1061-C1 | #1 C-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
26 | PS-IA1061-C2 | PS | IA1061-C2 | #1 COAL FEEDER C INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
27 | PS-IA1061-C2 | PS | IA1061-C2 | #1 C-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
7 | PS-IA1061-D1 | PS | IA1061-D1 | #1 COAL FEEDER D INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-052 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | DELETED 20150529 | 1 |  | COAL FEEDER
8 | PS-IA1061-D2 | PS | IA1061-D2 | #1 COAL FEEDER D INSTRUMENT AIR PRESSURE SWITCH LOW | PD-052 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | DELETED 20150529 | 1 |  | COAL FEEDER
13 | PSL-IA1706 | PSL | IA1706 | INSTRUMENT AIR UNIT NO.1 PRESSURE LOW SWITCH | PD-023-5/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0 |  | PS
11 | PSL-IA1706-NC | PSL | IA1706-NC | INSTRUMENT AIR UNIT NO.1 PRESSURE NOT LOW SWITCH | PD-023,5/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0 |  | PS
26 | PSLL-FG1085 | PSLL | FG1085 | #1 FURNACE PRESSURE SWITCH LOW-LOW (A) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
27 | PSLL-FG1085-NC | PSLL | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (A) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
28 | PSLL-FG1086 | PSLL | FG1086 | #1 FURNACE PRESSURE SWITCH LOW-LOW (B) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
29 | PSLL-FG1086-NC | PSLL | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (B) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
30 | PSLL-FG1087 | PSLL | FG1087 | #1 FURNACE PRESSURE SWITCH LOW-LOW (C) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
31 | PSLL-FG1087-NC | PSLL | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (C) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
11 | PSLL-LO1753 | PSLL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE LOW LOW SWITCH | PD-052 | - | - | 0~6Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
9 | PSLL-LO1756 | PSLL | LO1756 | #1 INDUCED DRAFT FAN LUBE OIL PRESSURE SWITCH LOW-LOW AT DOWNSTREAM OF LUBE OIL FILTER | PD-051 | - | - | 0~2.55 Kg/c㎡G | DI | FIELD | ARP | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
10 | PSL-LO1753 | PSL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE LOW SWITCH | PD-052 | - | - | 0~10Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
8 | PSL-LO1756 | PSL | LO1756 | #1 INDUCED DRAFT FAN LUBE OIL PRESSURE SWITCH LOW AT DOWNSTREAM OF LUBE OIL FILTER | PD-051 | - | - | 0~2.55 Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
5 | PS-LO1115-A1 | PS | LO1115-A1 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-1 (LOW ALARM/STANDBY PUMP START) | PD-017 | - | - | 1.5 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
6 | PS-LO1115-A2 | PS | LO1115-A2 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-2 (NORMAL/START PERMISIVE FOR BFP) | PD-017 | - | - | 2.0 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
7 | PS-LO1115-A3 | PS | LO1115-A3 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-3 (LOW-LOW/MAIN EQUIPMENT TRIP) | PD-017 | - | - | 1 | DI | FIELD | ARP | - | PACKAGE (BFP) |  | 0 |  | PS
8 | PS-LO1115-B1 | PS | LO1115-B1 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-1 (LOW ALARM/STANDBY PUMP START) | PD-017 | - | - | 1.5 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
9 | PS-LO1115-B2 | PS | LO1115-B2 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-2 (NORMAL/START PERMISIVE FOR BFP) | PD-017 | - | - | 2.0 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
10 | PS-LO1115-B3 | PS | LO1115-B3 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-3 (LOW-LOW/MAIN EQUIPMENT TRIP) | PD-017 | - | - | 1 | DI | FIELD | ARP | - | PACKAGE (BFP) |  | 0 |  | PS
14 | PSL-PA1043-A1 | PSL | PA1043-A1 | #1 BURNER(A) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,2/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
60 | PSL-PA1043-B1 | PSL | PA1043-B1 | #1 BURNER(B) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,3/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
106 | PSL-PA1043-C1 | PSL | PA1043-C1 | #1 BURNER(C) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,4/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
152 | PSL-PA1043-D1 | PSL | PA1043-D1 | #1 BURNER(D) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,5/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
12 | PSL-PA1705 | PSL | PA1705 | PLANT AIR TO UNIT NO.1 PRESSURE LOW SWITCH | PD-023-3/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0 |  | PS
15 | PT-AS1004 | PT | AS1004 | #1 AUXILIARY STEAM HEADER PRESSURE TRANSMITTER | PD-014 | 13 | 390 | 0~15 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
16 | PT-AS1005 | PT | AS1005 | #1 AUXILIARY STEAM HEADER PRESSURE TRANSMITTER | PD-014 | 13 | 390 | 0~15 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
26 | PT-BR1001-1 | PT | BR1001-1 | #1 DRUM PRESSURE TRANSMITTER-1 | PD-019 | 155 | 343 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
27 | PT-BR1001-2 | PT | BR1001-2 | #1 DRUM PRESSURE TRANSMITTER-2 | PD-019 | 155 | 343 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
28 | PT-BR1130 | PT | BR1130 | #1 SUPERHEATER PANEL NO.2 INLET STEAM PRESSURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
29 | PT-BR1150 | PT | BR1150 | #1 FINAL SUPERHEATER INLET STEAM PRESSURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
18 | PT-CD1104 | PT | CD1104 | #1 DEAERATOR PRESSURE TRANSMITTER | PD-016 | 8 | 380 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
19 | PT-CD1110 | PT | CD1110 | #1 CONDENSER PRESSURE TRANSMITTER | PD-016 | 1.055 & Full Vaccum | 100 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
20 | PT-CD1117 | PT | CD1117 | #1 CONDENSATE WATER PRESSURE TRANSMITTER | PD-016 | 24 | 65 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
21 | PT-CD1122 | PT | CD1122 | #1 DEAERATOR INLET CONDESATE PRESSURE TRANSMITTER | PD-016 | 24 | 200 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
5 | PT-CR1003 | PT | CR1003 | #1 COLD REHEAT STEAM PRESSURE TRANSMITTER | PD-012 | 45 | 395 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
6 | PT-CR1006 | PT | CR1006 | #1 REHEATER HEADER PRESSURE TRANSMITTER | PD-012 | 45 | 395 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
35 | PT-CW1152 | PT | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
36 | PT-CW1153 | PT | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
27 | PT-CW1156 | PT | CW1156 | #1 AUXILIARY COOLING WATER PRESSURE TRANSMITTER AT BOTTOM ASH SCREW CONVEYOR COMMON HEADER | PD-072 | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
37 | PT-DO0005 | PT | DO0005 | DIESEL OIL PUMP COMMON DISCHARGE PRESSURE TRANSMITTER | PD-022,1/5 | 25 | 70 | 0~25 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | PT
38 | PT-DO1008 | PT | DO1008 | #1 DIESEL OIL RETURN PRESSURE TRANSMITTER | PD-022,1/5 | 25 | 70 | 0~25 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | PT
15 | PT-DO1043-A2 | PT | DO1043-A2 | #1 BURNER(A) DIESEL OIL PRESSURE TRANSMITTER | PD-022,2/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
61 | PT-DO1043-B2 | PT | DO1043-B2 | #1 BURNER(B) DIESEL OIL PRESSURE TRANSMITTER | PD-022,3/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
107 | PT-DO1043-C2 | PT | DO1043-C2 | #1 BURNER(C) DIESEL OIL PRESSURE TRANSMITTER | PD-022,4/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
153 | PT-DO1043-D2 | PT | DO1043-D2 | #1 BURNER(D) DIESEL OIL PRESSURE TRANSMITTER | PD-022,5/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
73 | PT-FA1055-A | PT | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLETT PRESSURE TRANSMITTER | PD-054 | -330~8700 mmH2O | 149 | 0~10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
74 | PT-FA1055-B | PT | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET PRESSURE TRANSMITTER | PD-054 | -330~8700 mmH2O | 149 | 0~10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
69 | PT-FA1075 | PT | FA1075 | #1 PRIMARY AIR PREHEATER INLET AIR PRESSURE TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
70 | PT-FA1078 | PT | FA1078 | #1 PRIMARY AIR PREHEATER OUTLET AIR PRESSURE TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
71 | PT-FA1085 | PT | FA1085 | #1 SECONDARY AIR PREHEATER INLET AIR PRESSURE TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
72 | PT-FA1088 | PT | FA1088 | #1 SECONDARY AIR PREHEATER OUTLET AIR PRESSURE TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
56 | PT-FG1009-A1 | PT | FG1009-A1 | #1 CYCLONE A SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
57 | PT-FG1009-A2 | PT | FG1009-A2 | #1 CYCLONE A SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
58 | PT-FG1009-B1 | PT | FG1009-B1 | #1 CYCLONE B SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
59 | PT-FG1009-B2 | PT | FG1009-B2 | #1 CYCLONE B SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
60 | PT-FG1085 | PT | FG1085 | #1 FURNACE PRESSURE TRANSMITTER (A) | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
61 | PT-FG1086 | PT | FG1086 | #1 FURNACE PRESSURE TRANSMITTER (B) | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
62 | PT-FG1087-1 | PT | FG1087-1 | #1 FURNACE PRESSURE TRANSMITTER (C) -1 | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
63 | PT-FG1087-2 | PT | FG1087-2 | #1 FURNACE PRESSURE TRANSMITTER (C) -2 | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
64 | PT-FG1121 | PT | FG1121 | #1 AIR PRE-HEATER GAS INLET PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 371 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
65 | PT-FG1134 | PT | FG1134 | #1 AIR PRE-HEATER GAS OUTLET PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
66 | PT-FG1141-A | PT | FG1141-A | #1 INDUCED DRAFT FAN INLET FLUE GAS PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
67 | PT-FG1141-B | PT | FG1141-B | #1 INDUCED DRAFT FAN INLET FLUE GAS PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
68 | PT-FG1151 | PT | FG1151 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
22 | PT-FW1011 | PT | FW1011 | #1 BFP COMMON DISCHARGE WATER PRESSURE TRANSMITTER | PD-017 | 230 | 180 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
23 | PT-FW1115-A | PT | FW1115-A | #1 BFP(A) SUCTION PRESSURE TRANSMITTER | PD-017 | 10 | 180 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
24 | PT-FW1115-B | PT | FW1115-B | #1 BFP(B) SUCTION PRESSURE TRANSMITTER | PD-017 | 10 | 180 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
30 | PT-FW1160 | PT | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER PRESSURE TRANSMITTER | PD-019 | 230 | 275 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
25 | PT-HD1101 | PT | HD1101 | #1 LOW PRESSURE HEATER NO.1 STEAM PRESSURE TRANSMITTER | PD-018 | 3.5 & Full Vacuum | 150 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
7 | PT-HR1001 | PT | HR1001 | #1 REHEATER OUTLET HEADER PRESSURE TRANSMITTER | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
8 | PT-HR1003-1 | PT | HR1003-1 | #1 REHEAT STEAM PRESSURE TRANSMITTER-1 | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
9 | PT-HR1003-2 | PT | HR1003-2 | #1 REHEAT STEAM PRESSURE TRANSMITTER-2 | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
10 | PT-HR1011 | PT | HR1011 | #1 LP TURBINE BYPASS OUTLET PRESSURE TRANSMITTER | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
44 | PT-IA0107 | PT | IA0107 | INSTRUMENT AIR DRYER A OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
45 | PT-IA0127 | PT | IA0127 | INSTRUMENT AIR DRYER B OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
46 | PT-IA0147 | PT | IA0147 | INSTRUMENT AIR DRYER C OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
47 | PT-IA0706-A | PT | IA0706-A | INSTRUMENT AIR TANK A PRESSURE TRANSMITTER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
48 | PT-IA0706-B | PT | IA0706-B | INSTRUMENT AIR TANK B PRESSURE TRANSMITTER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
52 | PT-IA1064-A | PT | IA1064-A | # 1 AIR BUFFER TANK OF BIASING DAMPER A PRESSURE TRANSMITTER | PD-023,6/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
53 | PT-IA1064-B | PT | IA1064-B | # 1 AIR BUFFER TANK OF BIASING DAMPER B PRESSURE TRANSMITTER | PD-023,6/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
50 | PT-IA1128 | PT | IA1128 | #1 AIR BUFFER TANK OF TURNING GEAR PRESSURE TRANSMITTER | PD-023,4/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
51 | PT-IA1706 | PT | IA1706 | INSTRUMENT AIR UNIT NO.1 PRESSURE TRANSMITTER | PD-023,5/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
55 | PT-IW0715 | PT | IW0715 | INDUSTRIAL WATER PUMP COMMON HEADER PRESSURE TRANSMITTER | PD-025 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
1 | PT-MS1002 | PT | MS1002 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER PRESSURE TRANSMITTER | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
2 | PT-MS1006-1 | PT | MS1006-1 | #1 MAIN STEAM PRESSURE TRANSMITTER-1 | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
3 | PT-MS1006-2 | PT | MS1006-2 | #1 MAIN STEAM PRESSURE TRANSMITTER-2 | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
4 | PT-MS1021 | PT | MS1021 | #1 HP TURBINE BYPASS OUTLET PRESSURE TRANSMITTER | PD-011 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
54 | PT-MU0709 | PT | MU0709 | MAKE-UP PUMP COMMON HEADER PRESSURE TRANSMITTER | PD-024 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
39 | PT-PA0107 | PT | PA0107 | PA DRYER A OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
40 | PT-PA0127 | PT | PA0127 | PA DRYER B OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
41 | PT-PA0147 | PT | PA0147 | PA DRYER C OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
42 | PT-PA0705-A | PT | PA0705-A | PLANT AIR TANK A PRESSURE TRANSMITTER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
43 | PT-PA0705-B | PT | PA0705-B | PLANT AIR TANK B PRESSURE TRANSMITTER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
49 | PT-PA1705 | PT | PA1705 | PLANT AIR TO UNIT NO.1 PRESSURE TRANSMITTER | PD-023,3/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
4 | PT-SB1040 | PT | SB1040 | #1 HOT END SOOTBLOWER STEAM PRESSURE TRANSMITTER | - | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
5 | PT-SB1042 | PT | SB1042 | #1 COLD END SOOTBLOWER STEAM PRESSURE TRANSMITTER | - | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
17 | PT-SB1052 | PT | SB1052 | #1 SOOTBLOWING HEADER STEAM PRESSURE TRANSMITTER | PD-015 | 30 | 360 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
31 | PT-SW1110-A1 | PT | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
32 | PT-SW1110-A2 | PT | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
33 | PT-SW1110-B1 | PT | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
34 | PT-SW1110-B2 | PT | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
11 | PT-TS1013 | PT | TS1013 | #1 EXTRACTION STEAM NO.2 PRESSURE TRANSMITTER | PD-013 | 16 | 440 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
12 | PT-TS1017 | PT | TS1017 | #1 EXTRACTION STEAM NO.3 PRESSURE TRANSMITTER | PD-013 | 6.2 | 380 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
13 | PT-TS1022 | PT | TS1022 | #1 EXTRACTION STEAM NO.4 PRESSURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
14 | PT-TS1026 | PT | TS1026 | #1 EXTRACTION STEAM NO.5 PRESSURE TRANSMITTER | PD-013 | 3.6 | 285 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
28 | SE-CL1061-A | SE | CL1061-A | #1 A-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
29 | SE-CL1061-B | SE | CL1061-B | #1 B-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
30 | SE-CL1061-C | SE | CL1061-C | #1 C-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
6 | SE-FA1052-1 | SE | FA1052-1 | #1 AIR PRE-HEATER ROTOR SPEED SENSOR-1 | - | - | - | 0-12 mm | AI | FIELD | SM-1 | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
7 | SE-FA1052-2 | SE | FA1052-2 | #1 AIR PRE-HEATER ROTOR SPEED SENSOR-2 | - | - | - | 0-12 mm | AI | FIELD | SM-2 | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
10 | SE-LO1756 | SE | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING PICK UP SPEED | PD-051 | - | - | - | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
28 | SS-BH1060-A | SS | BH1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
29 | SS-BH1060-B | SS | BH1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
30 | SS-BH1060-C | SS | BH1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
31 | SS-BH1060-D | SS | BH1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
8 | ST-FA1502-1 | ST | FA1502-1 | #1 AIR PRE-HEATER ROTOR SPEED MONITOR-1 | - | - | - | 0-20000 | AI | LCP | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
9 | ST-FA1502-2 | ST | FA1502-2 | #1 AIR PRE-HEATER ROTOR SPEED MONITOR-2 | - | - | - | 0-20000 | AI | LCP | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
11 | ST-LO1756 | ST | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING PICK UP SPEED TRANSMITTER | PD-051 | - | - | 1200rpm | WET 4~20mA | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
12 | SV-CD1004 | SV | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
13 | SV-CD1005 | SV | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
14 | SV-CD1006 | SV | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
15 | SV-CD1104-2 | SV | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
16 | SV-CD1114 | SV | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
17 | SV-CD1115 | SV | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE SOLENOID VALVE(QUICK OPEN) | PD-016 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
18 | SV-CD1123 | SV | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
19 | SV-CD1125 | SV | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
31 | SV-CL1061-A7 | SV | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
32 | SV-CL1061-B7 | SV | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
33 | SV-CL1061-C7 | SV | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
1 | SV-CR1011 | SV | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
2 | SV-CR1012 | SV | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
16 | SV-DO1043-A1 | SV | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
17 | SV-DO1043-A2 | SV | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
62 | SV-DO1043-B1 | SV | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
63 | SV-DO1043-B2 | SV | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
108 | SV-DO1043-C1 | SV | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
109 | SV-DO1043-C2 | SV | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
154 | SV-DO1043-D1 | SV | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
155 | SV-DO1043-D2 | SV | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
20 | SVE-DO1043-A4 | SVE | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 EXTENDING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
21 | SVE-DO1043-A5 | SVE | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
66 | SVE-DO1043-B4 | SVE | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 EXTRENDING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
67 | SVE-DO1043-B5 | SVE | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 EXTRENDING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
112 | SVE-DO1043-C4 | SVE | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 RETRACTING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
113 | SVE-DO1043-C5 | SVE | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
158 | SVE-DO1043-D4 | SVE | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 RETRACTING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
159 | SVE-DO1043-D5 | SVE | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
10 | SV-FA1052-1 | SV | FA1052-1 | #1 AIR PRE-HEATER SOLENOID FOR AIR MOTOR | - | - | 0-10 BarG | - | DO | DCS | LOCAL INVERTER PANEL | 24VDC | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
11 | SV-FA1055-A2 | SV | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
12 | SV-FA1055-A3 | SV | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
13 | SV-FA1055-B2 | SV | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
14 | SV-FA1055-B3 | SV | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
31 | SV-FS1005 | SV | FS1005 | #1 FLASH PIPE DRAIN VALVE SOLENOID VALVE | PD-027 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
20 | SV-FW1060 | SV | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE SOLENOID VALVE(QUICK OPEN) | PD-017 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
21 | SV-FW1061 | SV | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
22 | SV-FW1111-1 | SV | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
23 | SV-FW1111-2 | SV | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
24 | SV-FW1121-1 | SV | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
25 | SV-FW1121-2 | SV | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
26 | SV-FW1151 | SV | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
6 | SV-HR1010 | SV | HR1010 | #1 LP TURBINE BYPASS VALVE SOLENOID VALVE(QUICK OPEN) | PD-012 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
7 | SV-HR1010-1 | SV | HR1010-1 | #1 LP TURBINE BYPASS VALVE WARMING VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
8 | SV-HR1021 | SV | HR1021 | #1 ILP TURBINE LINEDRAIN POT DP-HR01 DRAIN VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
9 | SV-HR1022 | SV | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
28 | SV-IW0113 | SV | IW0113 | TURBINE BUILDING PLUMBING WATER TK INLET SOLENOID VALVE | PD-025 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
3 | SV-MS1011 | SV | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
4 | SV-MS1020 | SV | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE SOLENOID VALVE (QUICK OPEN) | PD-011 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
5 | SV-MS1023 | SV | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
27 | SV-MU1109 | SV | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE SOLENOID VALVE | PD-021 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
18 | SV-PA1043-A2 | SV | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
19 | SV-PA1043-A3 | SV | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
64 | SV-PA1043-B2 | SV | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
65 | SV-PA1043-B3 | SV | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
110 | SV-PA1043-C2 | SV | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
111 | SV-PA1043-C3 | SV | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
156 | SV-PA1043-D2 | SV | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
157 | SV-PA1043-D3 | SV | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
4 | SV-PA1066A~I | SV | PA1066A~I | #1 COAL BUNKER A (T-1008A) AIR CANNON SOLENOID VALVE SV-PA1066A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
5 | SV-PA1067A~I | SV | PA1067A~I | #1 COAL BUNKER B (T-1008B) AIR CANNON SOLENOID VALVE SV-PA1067A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
6 | SV-PA1068A~I | SV | PA1068A~I | #1 COAL BUNKER C (T-1008C) AIR CANNON SOLENOID VALVE SV-PA1068A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
29 | SV-PW0114 | SV | PW0114 | TURBINE BUILDING POTABLE WATER TK INLET SOLENOID VALVE | PD-026 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
30 | SV-PW0721 | SV | PW0721 | WATER TREATMENT PLANT CONTROL BUILDING POTABLE WATER TANK INLET SOLENOID VALVE | PD-026 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
22 | SVR-DO1043-A5 | SVR | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
68 | SVR-DO1043-B5 | SVR | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
114 | SVR-DO1043-C5 | SVR | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
160 | SVR-DO1043-D5 | SVR | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
10 | SV-SB1054 | SV | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE SOLENOID VALVE | PD-015 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
11 | SV-SB1059 | SV | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE SOLENOID VALVE | PD-015 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
14 | TCV-CD1115 | TCV | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
15 | TCV-CD1124 | TCV | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
16 | TCV-CD1126 | TCV | CD1126 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
35 | TCV-CW1201 | TCV | CW1201 | #1 STEAM TURBINE LUBE OIL TEMPERATURE CONTROL VALVE | PD-021 | 10 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
39 | TCV-FG1116-A | TCV | FG1116-A | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-1 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
40 | TCV-FG1116-B | TCV | FG1116-B | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-2 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
41 | TCV-FG1116-C | TCV | FG1116-C | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-3 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
42 | TCV-FG1116-D | TCV | FG1116-D | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-4 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
43 | TCV-FG1117-A | TCV | FG1117-A | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-1 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
44 | TCV-FG1117-B | TCV | FG1117-B | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-2 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
45 | TCV-FG1117-C | TCV | FG1117-C | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-3 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
46 | TCV-FG1117-D | TCV | FG1117-D | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-4 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
19 | TCV-FW1060 | TCV | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 100 | 180 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
20 | TCV-FW1110-1 | TCV | FW1110-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
21 | TCV-FW1110-2 | TCV | FW1110-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
22 | TCV-FW1120-1 | TCV | FW1120-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
23 | TCV-FW1120-2 | TCV | FW1120-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
24 | TCV-FW1150 | TCV | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 100 | 180 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
30 | TE-AS1001 | TE | AS1001 | #1 MAIN STEAM DESUPERHEATING DOWNSTREAM TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
31 | TE-AS1003 | TE | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
32 | TE-AS1015 | TE | AS1015 | #1 GLAND STEAM DESUPERHEATING OUTLET TEMPERATURE ELEMENT | PD-014 | 13 | 300 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
32 | TE-BH1060-A1 | TE | BH1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
33 | TE-BH1060-A2 | TE | BH1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
34 | TE-BH1060-B1 | TE | BH1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
35 | TE-BH1060-B2 | TE | BH1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
36 | TE-BH1060-C1 | TE | BH1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
37 | TE-BH1060-C2 | TE | BH1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
38 | TE-BH1060-D1 | TE | BH1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
39 | TE-BH1060-D2 | TE | BH1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
94 | TE-BR1020 | TE | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
95 | TE-BR1030 | TE | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
96 | TE-BR1040 | TE | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
97 | TE-BR1110 | TE | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
98 | TE-BR1120-1 | TE | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-1 | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
99 | TE-BR1120-2 | TE | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-2 | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
100 | TE-BR1130-1 | TE | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
101 | TE-BR1130-2 | TE | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
102 | TE-BR1140-1 | TE | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
103 | TE-BR1140-2 | TE | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
104 | TE-BR1150-1 | TE | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
105 | TE-BR1150-2 | TE | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
35 | TE-CD1101 | TE | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
36 | TE-CD1102 | TE | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
37 | TE-CD1103-1 | TE | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
38 | TE-CD1103-2 | TE | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
39 | TE-CD1104 | TE | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE ELEMENT | PD-016 | 8 | 170 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
40 | TE-CD1110-1 | TE | CD1110-1 | #1 CONDENSER HOT WELL STEAM TEMPERATURE ELEMENT-1 | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
41 | TE-CD1110-2 | TE | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE ELEMENT-2 | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
42 | TE-CD1110-3 | TE | CD1110-3 | #1 CONDENSER NECK TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
43 | TE-CD1110-4 | TE | CD1110-4 | #1 CONDENSER FLASH CHAMBER TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
44 | TE-CD1116-A1 | TE | CD1116-A1 | #1 CONDENSAT PUMP (A) COUPLING TEMPERATURE ELEMENT | PD-016 | - | - | 0~120 | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
45 | TE-CD1116-A3 | TE | CD1116-A3 | #1 CONDENSAT PUMP (A) MOTOR BEARING DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
46 | TE-CD1116-A4 | TE | CD1116-A4 | #1 CONDENSAT PUMP (A) MOTOR BEARING NON-DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
47 | TE-CD1116-AU1 | TE | CD1116-AU1 | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
48 | TE-CD1116-AU2 | TE | CD1116-AU2 | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
49 | TE-CD1116-AV1 | TE | CD1116-AV1 | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
50 | TE-CD1116-AV2 | TE | CD1116-AV2 | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
51 | TE-CD1116-AW1 | TE | CD1116-AW1 | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
52 | TE-CD1116-AW2 | TE | CD1116-AW2 | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
53 | TE-CD1116-B1 | TE | CD1116-B1 | #1 CONDENSAT PUMP (B) COUPLING TEMPERATURE ELEMENT | PD-016 | - | - | 0~120 | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
54 | TE-CD1116-B3 | TE | CD1116-B3 | #1 CONDENSAT PUMP (B) MOTOR BEARING DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
55 | TE-CD1116-B4 | TE | CD1116-B4 | #1 CONDENSAT PUMP (B) MOTOR BEARING NON-DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
56 | TE-CD1116-BU1 | TE | CD1116-BU1 | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
57 | TE-CD1116-BU2 | TE | CD1116-BU2 | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
58 | TE-CD1116-BV1 | TE | CD1116-BV1 | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
59 | TE-CD1116-BV2 | TE | CD1116-BV2 | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
60 | TE-CD1116-BW1 | TE | CD1116-BW1 | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
61 | TE-CD1116-BW2 | TE | CD1116-BW2 | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
62 | TE-CD1118 | TE | CD1118 | #1 CONDENSATE WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
63 | TE-CD1119 | TE | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
64 | TE-CD1120 | TE | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
65 | TE-CD1122 | TE | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
16 | TE-CR1004 | TE | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
17 | TE-CR1005-1 | TE | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
18 | TE-CR1005-2 | TE | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
40 | TE-CW1060-A1 | TE | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
41 | TE-CW1060-A2 | TE | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
42 | TE-CW1060-B1 | TE | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
43 | TE-CW1060-B2 | TE | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
44 | TE-CW1060-C1 | TE | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
45 | TE-CW1060-C2 | TE | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
46 | TE-CW1060-D1 | TE | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
47 | TE-CW1060-D2 | TE | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
141 | TE-CW1108-A3 | TE | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR BEARING TEMPERATURE-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
142 | TE-CW1108-A4 | TE | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR BEARING TEMPERATURE-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
143 | TE-CW1108-AU1 | TE | CW1108-AU1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
144 | TE-CW1108-AU2 | TE | CW1108-AU2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
145 | TE-CW1108-AV1 | TE | CW1108-AV1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
146 | TE-CW1108-AV2 | TE | CW1108-AV2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
147 | TE-CW1108-AW1 | TE | CW1108-AW1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
148 | TE-CW1108-AW2 | TE | CW1108-AW2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
149 | TE-CW1108-B3 | TE | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR BEARING TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
150 | TE-CW1108-B4 | TE | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR BEARING TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
151 | TE-CW1108-BU1 | TE | CW1108-BU1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
152 | TE-CW1108-BU2 | TE | CW1108-BU2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
153 | TE-CW1108-BV1 | TE | CW1108-BV1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
154 | TE-CW1108-BV2 | TE | CW1108-BV2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
155 | TE-CW1108-BW1 | TE | CW1108-BW1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
156 | TE-CW1108-BW2 | TE | CW1108-BW2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
157 | TE-CW1152 | TE | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
158 | TE-CW1153 | TE | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
1 | TE-CW1156 | TE | CW1156 | #1 AUXILIARY COOLING WATER TEMPERATURE ELEMENT AT ASH CONVEYOR COMMON HEADER | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
11 | TE-FA1052-1 | TE | FA1052-1 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-1 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
12 | TE-FA1052-2 | TE | FA1052-2 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-2 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
13 | TE-FA1052-3 | TE | FA1052-3 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-3 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
14 | TE-FA1052-4 | TE | FA1052-4 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-4 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
15 | TE-FA1052-5 | TE | FA1052-5 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-5 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
16 | TE-FA1052-6 | TE | FA1052-6 | #1 AIR PRE-HEATER TOP BEARING TEMPERATUTRE | - | - | - | -200~850℃ | AI | FIELD | TT | RTD | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
17 | TE-FA1052-7 | TE | FA1052-7 | #1 AIR PRE-HEATER BOOTOM BEARING TEMPERATUTRE | - | - | - | -200~850℃ | AI | FIELD | TT | RTD | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
2 | TE-FA1053-1 | TE | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
3 | TE-FA1053-2 | TE | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
4 | TE-FA1053-3 | TE | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
5 | TE-FA1053-4 | TE | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
6 | TE-FA1053-U1 | TE | FA1053-U1 | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
7 | TE-FA1053-U2 | TE | FA1053-U2 | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
8 | TE-FA1053-V1 | TE | FA1053-V1 | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
9 | TE-FA1053-V2 | TE | FA1053-V2 | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
10 | TE-FA1053-W1 | TE | FA1053-W1 | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
11 | TE-FA1053-W2 | TE | FA1053-W2 | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
24 | TE-FA1054-1 | TE | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
25 | TE-FA1054-2 | TE | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
26 | TE-FA1054-3 | TE | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
27 | TE-FA1054-4 | TE | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
28 | TE-FA1054-U1 | TE | FA1054-U1 | #1 SECONDARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
29 | TE-FA1054-U2 | TE | FA1054-U2 | #1 SECONDARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
30 | TE-FA1054-V1 | TE | FA1054-V1 | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
31 | TE-FA1054-V2 | TE | FA1054-V2 | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
32 | TE-FA1054-W1 | TE | FA1054-W1 | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
33 | TE-FA1054-W2 | TE | FA1054-W2 | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
214 | TE-FA1055-A | TE | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
15 | TE-FA1055-A1 | TE | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
16 | TE-FA1055-A2 | TE | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
17 | TE-FA1055-A3 | TE | FA1055-A3 | #1 FLUIDIZING AIR BLOWER(A) MOTOR FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
18 | TE-FA1055-A4 | TE | FA1055-A4 | #1 FLUIDIZING AIR BLOWER(A) MOTOR REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
19 | TE-FA1055-AU1 | TE | FA1055-AU1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-U1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
20 | TE-FA1055-AU2 | TE | FA1055-AU2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-U2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
21 | TE-FA1055-AV1 | TE | FA1055-AV1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-V1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
22 | TE-FA1055-AV2 | TE | FA1055-AV2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-V2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
23 | TE-FA1055-AW1 | TE | FA1055-AW1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE -W1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
24 | TE-FA1055-AW2 | TE | FA1055-AW2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE -W2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
215 | TE-FA1055-B | TE | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
25 | TE-FA1055-B1 | TE | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
26 | TE-FA1055-B2 | TE | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
27 | TE-FA1055-B3 | TE | FA1055-B3 | #1 FLUIDIZING AIR BLOWER(B) MOTOR FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
28 | TE-FA1055-B4 | TE | FA1055-B4 | #1 FLUIDIZING AIR BLOWER(B) MOTOR REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
29 | TE-FA1055-BU1 | TE | FA1055-BU1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-U1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
30 | TE-FA1055-BU2 | TE | FA1055-BU2 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-U2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
31 | TE-FA1055-BV1 | TE | FA1055-BV1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-V1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
32 | TE-FA1055-BV1 | TE | FA1055-BV1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-V2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
33 | TE-FA1055-BW1 | TE | FA1055-BW1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-W1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
34 | TE-FA1055-BW2 | TE | FA1055-BW2 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-W2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
204 | TE-FA1072 | TE | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-052 | 0 | 66 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
205 | TE-FA1073 | TE | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
206 | TE-FA1074 | TE | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-052 | -340~2500 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
207 | TE-FA1076 | TE | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
208 | TE-FA1077 | TE | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-052 | -340~2500 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
209 | TE-FA1082 | TE | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-053 | 0 | 66 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
210 | TE-FA1083 | TE | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
211 | TE-FA1084 | TE | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
212 | TE-FA1086 | TE | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
213 | TE-FA1087 | TE | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
159 | TE-FG1009-A | TE | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
160 | TE-FG1009-B | TE | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
12 | TE-FG1056-1 | TE | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
13 | TE-FG1056-2 | TE | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
14 | TE-FG1056-3 | TE | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
15 | TE-FG1056-4 | TE | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
16 | TE-FG1056-U1 | TE | FG1056-U1 | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
17 | TE-FG1056-U2 | TE | FG1056-U2 | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
18 | TE-FG1056-V1 | TE | FG1056-V1 | #1 INDUCED DRAFT FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
19 | TE-FG1056-V2 | TE | FG1056-V2 | #1 INDUCED DRAFT FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
20 | TE-FG1056-W1 | TE | FG1056-W1 | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
21 | TE-FG1056-W2 | TE | FG1056-W2 | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
161 | TE-FG1057-8 | TE | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | - | PACKAGE (CEMS) |  | 0 |  | TE
162 | TE-FG1090-A | TE | FG1090-A | #1 FURNACE FRONT TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
163 | TE-FG1090-B | TE | FG1090-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
164 | TE-FG1090-C | TE | FG1090-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
165 | TE-FG1090-D | TE | FG1090-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
166 | TE-FG1090-E | TE | FG1090-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
167 | TE-FG1090-F | TE | FG1090-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
168 | TE-FG1090-G | TE | FG1090-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
169 | TE-FG1090-H | TE | FG1090-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
170 | TE-FG1090-I | TE | FG1090-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
171 | TE-FG1091-A | TE | FG1091-A | #1 FURNACE FRONT TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
172 | TE-FG1091-B | TE | FG1091-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
173 | TE-FG1091-C | TE | FG1091-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
174 | TE-FG1091-D | TE | FG1091-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
175 | TE-FG1091-E | TE | FG1091-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
176 | TE-FG1091-F | TE | FG1091-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
177 | TE-FG1091-G | TE | FG1091-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
178 | TE-FG1091-H | TE | FG1091-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
179 | TE-FG1091-I | TE | FG1091-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
180 | TE-FG1092-A | TE | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
181 | TE-FG1092-B | TE | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
182 | TE-FG1095-A | TE | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
183 | TE-FG1095-B | TE | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
184 | TE-FG1096-A | TE | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
185 | TE-FG1096-B | TE | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
186 | TE-FG1100 | TE | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
187 | TE-FG1101 | TE | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
188 | TE-FG1102 | TE | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
189 | TE-FG1103 | TE | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
190 | TE-FG1104 | TE | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 600 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
191 | TE-FG1105 | TE | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 620 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
192 | TE-FG1106 | TE | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
193 | TE-FG1107 | TE | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 590 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
194 | TE-FG1108 | TE | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 480 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
195 | TE-FG1109 | TE | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
196 | TE-FG1110 | TE | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE ELEMENT-A | PD-051 | ±890mmH2O | 430 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
197 | TE-FG1111 | TE | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 450 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
198 | TE-FG1113 | TE | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE ELEMENT-B | PD-051 | ±890mmH2O | 430 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
199 | TE-FG1124 | TE | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 371 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
200 | TE-FG1125 | TE | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(B) | PD-051 | ±890mmH2O | 371 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
201 | TE-FG1132 | TE | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
202 | TE-FG1133 | TE | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
203 | TE-FG1152 | TE | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
66 | TE-FW1010 | TE | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 10 | 180 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
67 | TE-FW1011 | TE | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE ELEMENT | PD-017 | 230 | 180 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
68 | TE-FW1105 | TE | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 220 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
69 | TE-FW1106 | TE | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 275 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
70 | TE-FW1115-A1 | TE | FW1115-A1 | #1 BFP(A) PUMP SIDE BEARING FRONT(NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
71 | TE-FW1115-A2 | TE | FW1115-A2 | #1 BFP(A) PUMP BEARING REAR(DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
72 | TE-FW1115-A3 | TE | FW1115-A3 | #1 BFP(A) MOTOR SIDE BEARING REAR (DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
73 | TE-FW1115-A4 | TE | FW1115-A4 | #1 BFP(A) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
74 | TE-FW1115-AU1 | TE | FW1115-AU1 | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
75 | TE-FW1115-AU2 | TE | FW1115-AU2 | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
76 | TE-FW1115-AV1 | TE | FW1115-AV1 | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
77 | TE-FW1115-AV2 | TE | FW1115-AV2 | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
78 | TE-FW1115-AW1 | TE | FW1115-AW1 | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
79 | TE-FW1115-AW2 | TE | FW1115-AW2 | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
80 | TE-FW1115-B1 | TE | FW1115-B1 | #1 BFP(B) PUMP BEARING FRONT(NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
81 | TE-FW1115-B2 | TE | FW1115-B2 | #1 BFP(B) PUMP BEARING REAR(DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
82 | TE-FW1115-B3 | TE | FW1115-B3 | #1 BFP(B) MOTOR SIDE BEARING REAR (DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
83 | TE-FW1115-B4 | TE | FW1115-B4 | #1 BFP(B) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
84 | TE-FW1115-BU-1 | TE | FW1115-BU-1 | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
85 | TE-FW1115-BU-2 | TE | FW1115-BU-2 | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-017 |  |  | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
86 | TE-FW1115-BV-1 | TE | FW1115-BV-1 | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
87 | TE-FW1115-BV-2 | TE | FW1115-BV-2 | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-017 |  |  | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
88 | TE-FW1115-BW-1 | TE | FW1115-BW-1 | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
89 | TE-FW1115-BW-2 | TE | FW1115-BW-2 | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
106 | TE-FW1160 | TE | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 230 | 275 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
90 | TE-HD1102 | TE | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 150 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
91 | TE-HD1103 | TE | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
92 | TE-HD1105 | TE | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE ELEMENT | PD-018 | 16 & Full Vaccum | 210 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
93 | TE-HD1106 | TE | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 45 & Full Vaccum | 260 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
19 | TE-HR1002-1 | TE | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
20 | TE-HR1002-2 | TE | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
21 | TE-HR1004 | TE | HR1004 | #1 REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
22 | TE-HR1010 | TE | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OUTLET TEMPERATURE ELEMENT | PD-012 | - | - | - | - | FIELD | TT | T/C | PACKAGE (CV) | NEW ADDED | 0 |  | TE
23 | TE-HR1012-1 | TE | HR1012-1 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 15 | 280 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
24 | TE-HR1012-2 | TE | HR1012-2 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 15 | 280 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
11 | TE-MS1004-1 | TE | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-1 | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
12 | TE-MS1004-2 | TE | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-2 | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
13 | TE-MS1007 | TE | MS1007 | #1 MAIN STEAM TEMPERATURE ELEMENT | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
14 | TE-MS1022-1 | TE | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-011 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
15 | TE-MS1022-2 | TE | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-011 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
1 | TE-P0719-1 | TE | P0719-1 | FIRE PUMP(A) PUMP SIDE BEARING FRONT END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
2 | TE-P0719-2 | TE | P0719-2 | FIRE PUMP(A) PUMP SIDE BEARING REAR END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
3 | TE-P0719-3 | TE | P0719-3 | FIRE PUMP(A) MOTOR SIDE BEARING FRONT END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
4 | TE-P0719-4 | TE | P0719-4 | FIRE PUMP(A) MOTOR SIDE BEARING REAR END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
5 | TE-P0719-U1 | TE | P0719-U1 | FIRE PUMP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
6 | TE-P0719-U2 | TE | P0719-U2 | FIRE PUMP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
7 | TE-P0719-V1 | TE | P0719-V1 | FIRE PUMP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
8 | TE-P0719-V2 | TE | P0719-V2 | FIRE PUMP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
9 | TE-P0719-W1 | TE | P0719-W1 | FIRE PUMP(A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
10 | TE-P0719-W2 | TE | P0719-W2 | FIRE PUMP(A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
33 | TE-SB1056 | TE | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
34 | TE-SB1057 | TE | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
107 | TE-SW1110-A1 | TE | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
108 | TE-SW1110-A2 | TE | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
109 | TE-SW1110-B1 | TE | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
110 | TE-SW1110-B2 | TE | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
111 | TE-SW1501-A31 | TE | SW1501-A31 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
112 | TE-SW1501-A32 | TE | SW1501-A32 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
113 | TE-SW1501-A41 | TE | SW1501-A41 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
114 | TE-SW1501-A42 | TE | SW1501-A42 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
115 | TE-SW1501-AU1 | TE | SW1501-AU1 | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
116 | TE-SW1501-AU2 | TE | SW1501-AU2 | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
117 | TE-SW1501-AV1 | TE | SW1501-AV1 | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
118 | TE-SW1501-AV2 | TE | SW1501-AV2 | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
119 | TE-SW1501-AW1 | TE | SW1501-AW1 | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
120 | TE-SW1501-AW2 | TE | SW1501-AW2 | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
121 | TE-SW1501-B31 | TE | SW1501-B31 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
122 | TE-SW1501-B32 | TE | SW1501-B32 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
123 | TE-SW1501-B41 | TE | SW1501-B41 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
124 | TE-SW1501-B42 | TE | SW1501-B42 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
125 | TE-SW1501-BU1 | TE | SW1501-BU1 | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
126 | TE-SW1501-BU2 | TE | SW1501-BU2 | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
127 | TE-SW1501-BV1 | TE | SW1501-BV1 | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
128 | TE-SW1501-BV2 | TE | SW1501-BV2 | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
129 | TE-SW1501-BW1 | TE | SW1501-BW1 | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
130 | TE-SW1501-BW2 | TE | SW1501-BW2 | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
131 | TE-SW1501-C31 | TE | SW1501-C31 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
132 | TE-SW1501-C32 | TE | SW1501-C32 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
133 | TE-SW1501-C41 | TE | SW1501-C41 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
134 | TE-SW1501-C42 | TE | SW1501-C42 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
135 | TE-SW1501-CU1 | TE | SW1501-CU1 | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
136 | TE-SW1501-CU2 | TE | SW1501-CU2 | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
137 | TE-SW1501-CV1 | TE | SW1501-CV1 | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
138 | TE-SW1501-CV2 | TE | SW1501-CV2 | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
139 | TE-SW1501-CW1 | TE | SW1501-CW1 | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
140 | TE-SW1501-CW2 | TE | SW1501-CW2 | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
25 | TE-TS1011 | TE | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-013 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
26 | TE-TS1014 | TE | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE ELEMENT | PD-013 | 16 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
27 | TE-TS1018 | TE | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE ELEMENT | PD-013 | 6.2 | 380 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
28 | TE-TS1023 | TE | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
29 | TE-TS1027 | TE | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
7 | TG-AS1002 | TG | AS1002 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE GAUGE | PD-014 | 13 | 390 | 0~600 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
8 | TG-AS1016 | TG | AS1016 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE GAUGE | PD-014 | 13 | 300 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
13 | TG-CD1104-1 | TG | CD1104-1 | #1 DEAERATOR TEMPERATURE GAUGE | PD-016 | 8 | 380 | 0~400 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
14 | TG-CD1104-2 | TG | CD1104-2 | #1 DEAERATOR STORAGE TANK TEMPERATURE GAUGE | PD-016 | 8 | 170 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
15 | TG-CD1110-1 | TG | CD1110-1 | #1 CONDENSER HOT WELL WATER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
16 | TG-CD1110-2 | TG | CD1110-2 | #1 CONDENSER FLASH CHAMBER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
95 | TG-CD1116-A | TG | CD1116-A | #1 CONDENSATE PUMP (A) COUPLING TEMPERATURE DAUGE | PD-016 | - | - | later | - | - | - | - | PACKAGE (CONDENSATE PUMP) | DELETED | 0 |  | TG
96 | TG-CD1116-B | TG | CD1116-B | #1 CONDENSATE PUMP (B) COUPLING TEMPERATURE DAUGE | PD-016 | - | - | later | - | - | - | - | PACKAGE (CONDENSATE PUMP) | DELETED | 0 |  | TG
17 | TG-CD1118 | TG | CD1118 | #1 CONDENSATE WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
18 | TG-CD1119 | TG | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
9 | TG-CD1119-1 | TG | CD1119-1 | #1 STEAM JET AIR EJECTOR CONDENSER COOLING WATER INLET TEMPERATURE GAUGE | PD-014 | - | 44 | 0~100 | - | - | - | - | PACKAGE (AIR EJECTOR) | NEW ADDED | 0 |  | TG
10 | TG-CD1119-2 | TG | CD1119-2 | #1 STEAM JET AIR EJECTOR CONDENSER COOLING WATER OUTLET TEMPERATURE GAUGE | PD-014 | - | 49.5 | 0~100 | - | - | - | - | PACKAGE (AIR EJECTOR) | NEW ADDED | 0 |  | TG
19 | TG-CD1120 | TG | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
48 | TG-CW1060-A | TG | CW1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
49 | TG-CW1060-A1 | TG | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
50 | TG-CW1060-A2 | TG | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
51 | TG-CW1060-B | TG | CW1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
52 | TG-CW1060-B1 | TG | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
53 | TG-CW1060-B2 | TG | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
54 | TG-CW1060-C | TG | CW1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
55 | TG-CW1060-C1 | TG | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
56 | TG-CW1060-C2 | TG | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
57 | TG-CW1060-D | TG | CW1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
58 | TG-CW1060-D1 | TG | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
59 | TG-CW1060-D2 | TG | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
59 | TG-CW1107-A | TG | CW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
60 | TG-CW1107-B | TG | CW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
61 | TG-CW1107-C | TG | CW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
62 | TG-CW1115-A1 | TG | CW1115-A1 | #1 BFP MOTOR P-1115A COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
63 | TG-CW1115-B1 | TG | CW1115-B1 | #1 BFP MOTOR P-1115B COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
86 | TG-CW1140-3 | TG | CW1140-3 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY THERMOMETER | PD-044 | 5 | 40 | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
64 | TG-CW1151 | TG | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
65 | TG-CW1152 | TG | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
66 | TG-CW1154-A1 | TG | CW1154-A1 | #1 STEAM TURBINE LUBE OIL COOLER A INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
67 | TG-CW1154-A2 | TG | CW1154-A2 | #1 STEAM TURBINE LUBE OIL COOLER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
68 | TG-CW1154-B1 | TG | CW1154-B1 | #1 STEAM TURBINE LUBE OIL COOLER B INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
69 | TG-CW1154-B2 | TG | CW1154-B2 | #1 STEAM TURBINE LUBE OIL COOLER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
70 | TG-CW1155-A1 | TG | CW1155-A1 | #1 GENERATOR AIR COOLER A-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
71 | TG-CW1155-A2 | TG | CW1155-A2 | #1 GENERATOR AIR COOLER A-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
72 | TG-CW1155-A3 | TG | CW1155-A3 | #1 GENERATOR AIR COOLER A-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
73 | TG-CW1155-A4 | TG | CW1155-A4 | #1 GENERATOR AIR COOLER A-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
74 | TG-CW1155-B1 | TG | CW1155-B1 | #1 GENERATOR AIR COOLER B-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
75 | TG-CW1155-B2 | TG | CW1155-B2 | #1 GENERATOR AIR COOLER B-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
76 | TG-CW1155-B3 | TG | CW1155-B3 | #1 GENERATOR AIR COOLER B-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
77 | TG-CW1155-B4 | TG | CW1155-B4 | #1 GENERATOR AIR COOLER B-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
78 | TG-CW1155-C1 | TG | CW1155-C1 | #1 GENERATOR AIR COOLER C INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
79 | TG-CW1155-C2 | TG | CW1155-C2 | #1 GENERATOR AIR COOLER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
80 | TG-CW1155-D1 | TG | CW1155-D1 | #1 GENERATOR AIR COOLER D INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
81 | TG-CW1155-D2 | TG | CW1155-D2 | #1 GENERATOR AIR COOLER D OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
82 | TG-DO0003 | TG | DO0003 | DIESEL OIL PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
83 | TG-DO1006 | TG | DO1006 | #1 DIESEL OIL TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
20 | TG-FW1115-A1 | TG | FW1115-A1 | #1 BFP(A) PUMP DISCHARGE TEMPERATURE GAUGE | PD-017 | - | - | 0~300 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
21 | TG-FW1115-A2 | TG | FW1115-A2 | #1 BFP(A) PLAN 23 FLUSHING IN LINE DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
22 | TG-FW1115-A3 | TG | FW1115-A3 | #1 BFP(A) PLAN 23 FLUSHING IN LINE NON DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
23 | TG-FW1115-A4 | TG | FW1115-A4 | #1 BFP(A) PUMP DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
24 | TG-FW1115-A5 | TG | FW1115-A5 | #1 BFP(A) PUMP NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
25 | TG-FW1115-A6 | TG | FW1115-A6 | #1 BFP(A) MOTOR DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
26 | TG-FW1115-A7 | TG | FW1115-A7 | #1 BFP(A) MOTOR NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
27 | TG-FW1115-A8 | TG | FW1115-A8 | #1 BFP(A) COOLING WATER OUTLET HEADER TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
28 | TG-FW1115-B1 | TG | FW1115-B1 | #1 BFP(B) PUMP DISCHARGE TEMPERATURE GAUGE | PD-017 | - | - | 0~300 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
29 | TG-FW1115-B2 | TG | FW1115-B2 | #1 BFP(B) PLAN 23 FLUSHING IN LINE DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
30 | TG-FW1115-B3 | TG | FW1115-B3 | #1 BFP(B) PLAN 23 FLUSHING IN LINE NON DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
31 | TG-FW1115-B4 | TG | FW1115-B4 | #1 BFP(B) PUMP DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
32 | TG-FW1115-B5 | TG | FW1115-B5 | #1 BFP(B) PUMP NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
33 | TG-FW1115-B6 | TG | FW1115-B6 | #1 BFP(B) MOTOR DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
34 | TG-FW1115-B7 | TG | FW1115-B7 | #1 BFP(B) MOTOR NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
35 | TG-FW1115-B8 | TG | FW1115-B8 | #1 BFP(B) COOLING WATER OUTLET HEADER TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
46 | TG-FW1160 | TG | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE GAUGE | PD-019 | 230 | 275 | 0~400 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
42 | TG-HD1102 | TG | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 150 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
43 | TG-HD1103 | TG | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 200 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
44 | TG-HD1105 | TG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
45 | TG-HD1106 | TG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
85 | TG-IA0151 | TG | IA0151 | IA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-2/6 | 10 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
36 | TG-LO1115-A1 | TG | LO1115-A1 | #1 BFP(A) LUBE OIL COOLER INLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | TG
37 | TG-LO1115-A2 | TG | LO1115-A2 | #1 BFP(A) LUBE OIL COOLER OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | TG
38 | TG-LO1115-A3 | TG | LO1115-A3 | #1 BFP(A) LUBE OIL TANK TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | TG
39 | TG-LO1115-B1 | TG | LO1115-B1 | #1 BFP(B) LUBE OIL COOLER INLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0 |  | TG
40 | TG-LO1115-B2 | TG | LO1115-B2 | #1 BFP(B) LUBE OIL COOLER OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0 |  | TG
41 | TG-LO1115-B3 | TG | LO1115-B3 | #1 BFP(B) LUBE OIL TANK TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0 |  | TG
12 | TG-LO1753 | TG | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM TEMPERATURE GAUGE | PD-052 | - | - | 0~100℃ | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
22 | TG-LO1756-1 | TG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE GAUGE AT UPSTREAM OF HEAT EXCHANGER | PD-051 | - | - | 0~150℃ | - | - | - | BI-METAL | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
23 | TG-LO1756-2 | TG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE GAUGE AT DOWNSTREAM OF HEAT EXCHANGER | PD-051 | - | - | 0~150℃ | - | - | - | BI-METAL | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
1 | TG-MS1005 | TG | MS1005 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE GAUGE | PD-011 | 144 | 550 | 0~700 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
84 | TG-PA0151 | TG | PA0151 | PA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-1/6 | 10 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
11 | TG-SB1055 | TG | SB1055 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
12 | TG-SB1058 | TG | SB1058 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
87 | TG-SP1001 | TG | SP1001 | #1 DEAERATOR UPSTREAM THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
88 | TG-SP1002 | TG | SP1002 | #1 DEAERATOR OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
89 | TG-SP1003 | TG | SP1003 | #1 MAKE-UP WATER PUMP OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
90 | TG-SP1004 | TG | SP1004 | #1 ECONOMIZER INLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
91 | TG-SP1005 | TG | SP1005 | #1 DRUM WATER (BLOW DOWN) PRESSUE GAUGE | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
92 | TG-SP1006 | TG | SP1006 | #1 SATURATED STEAM THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
93 | TG-SP1007 | TG | SP1007 | #1 MAIN STEAM LINE THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
94 | TG-SP1008 | TG | SP1008 | #1 CONDENSATE PUMP OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
47 | TG-SW1107-A | TG | SW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
48 | TG-SW1107-B | TG | SW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
49 | TG-SW1107-C | TG | SW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
50 | TG-SW1110-A1 | TG | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
51 | TG-SW1110-A2 | TG | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
52 | TG-SW1110-B1 | TG | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
53 | TG-SW1110-B2 | TG | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
54 | TG-SW1503-A | TG | SW1503-A | #1 SEAWATER BOOSTER PUMP A SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
55 | TG-SW1503-B | TG | SW1503-B | #1 SEAWATER BOOSTER PUMP B SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
56 | TG-SW1503-C | TG | SW1503-C | #1 SEAWATER BOOSTER PUMP C SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
57 | TG-SW1551 | TG | SW1551 | #1 SEAWATER PUMP DISCHARGE HEADER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
58 | TG-SW1552 | TG | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
2 | TG-TS1012 | TG | TS1012 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE GAUGE | PD-013 | 45 | 395 | 0~600 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
3 | TG-TS1016 | TG | TS1016 | #1 EXTRACTION STEAM NO.2 TEMPERATURE GAUGE | PD-013 | 16 | 440 | 0~600 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
4 | TG-TS1021 | TG | TS1021 | #1 DEAERATOR INLET STEAM TEMPERATURE GAUGE | PD-013 | 6.2 | 380 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
5 | TG-TS1025 | TG | TS1025 | #1 EXTRACTION STEAM NO.4 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
6 | TG-TS1029 | TG | TS1029 | #1 EXTRACTION STEAM NO.5 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
86 | TS-AS1391 | TS | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
89 | TS-AS1392 | TS | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
92 | TS-AS1393 | TS | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
3 | TS-AS1394 | TS | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
95 | TS-AS1395 | TS | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
98 | TS-AS1396 | TS | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
208 | TS-AV1391 | TS | AV1391 | #1 CONDENSER VACUUM BREAKER MOV TORQUE SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
176 | TS-BD1001 | TS | BD1001 | #1 BOILER MASS BLOWDOWN MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
179 | TS-BD1002 | TS | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
182 | TS-BR1391 | TS | BR1391 | #1 SUPERHEATER PANEL NO.1 INLET TO REHEATER MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
111 | TS-CD1002 | TS | CD1002 | #1 LP HEATER NO.1 OUTLET CONDESATE SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
114 | TS-CD1003 | TS | CD1003 | #1 LP HEATER NO.1 CONDENSATE BYPASS MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
123 | TS-CD1007 | TS | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
126 | TS-CD1008 | TS | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
34 | TS-CL1061-A | TS | CL1061-A | #1 A-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
35 | TS-CL1061-B | TS | CL1061-B | #1 B-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
36 | TS-CL1061-C | TS | CL1061-C | #1 C-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
34 | TS-FA1005 | TS | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
35 | TS-FA1006 | TS | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
36 | TS-FA1007 | TS | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
37 | TS-FA1008 | TS | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
38 | TS-FA1009 | TS | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
39 | TS-FA1010 | TS | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
40 | TS-FA1011 | TS | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
41 | TS-FA1012 | TS | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
42 | TS-FA1013 | TS | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
43 | TS-FA1014 | TS | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
44 | TS-FA1015 | TS | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
45 | TS-FA1016 | TS | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
46 | TS-FA1017 | TS | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
47 | TS-FA1018 | TS | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
48 | TS-FA1019 | TS | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
49 | TS-FA1020 | TS | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
50 | TS-FA1021 | TS | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
51 | TS-FA1022 | TS | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
52 | TS-FA1023 | TS | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
53 | TS-FA1024 | TS | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
54 | TS-FA1025 | TS | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
55 | TS-FA1026 | TS | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
23 | TS-FA1043-A | TS | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
69 | TS-FA1043-B | TS | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
115 | TS-FA1043-C | TS | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
161 | TS-FA1043-D | TS | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
12 | TS-FA1053-1 | TS | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
56 | TS-FA1054-1 | TS | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
146 | TS-FW1001 | TS | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
149 | TS-FW1002 | TS | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
170 | TS-FW1391 | TS | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
173 | TS-FW1392 | TS | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
30 | TS-HR1391 | TS | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV TORQUE SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
205 | TS-IW0391 | TS | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV TORQUE SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
13 | TS-LO1753 | TS | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM TEMPERATURE SWITCH | PD-052 | - | - | 0~200℃ | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
24 | TS-LO1756-1 | TS | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE SWITCH HIGH | PD-051 | - | - | 0~160℃ | DI | FIELD | DCS | CAPILLIARY | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
25 | TS-LO1756-2 | TS | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE SWITCH HIGH-HIGH | PD-051 | - | - | 0~160℃ | DI | FIELD | ARP | CAPILLIARY | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
16 | TS-MS1391 | TS | MS1391 | #1 MAIN STEAM SHUT-OFF MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
19 | TS-MS1392 | TS | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
141 | TS-MU1001 | TS | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
101 | TS-SB1001 | TS | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV TORQUE SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
185 | TS-SW1001 | TS | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
188 | TS-SW1002 | TS | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
191 | TS-SW1003 | TS | SW1003 | #1 BALL VESSEL T-1116 INLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
194 | TS-SW1004 | TS | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
197 | TS-SW1005 | TS | SW1005 | #1 BALL VESSEL T-1115 INLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
200 | TS-SW1006 | TS | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
33 | TS-TS1001 | TS | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
36 | TS-TS1002 | TS | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
39 | TS-TS1003 | TS | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
45 | TS-TS1005 | TS | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
48 | TS-TS1389 | TS | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
51 | TS-TS1390 | TS | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
54 | TS-TS1391 | TS | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
57 | TS-TS1392 | TS | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
60 | TS-TS1393 | TS | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
63 | TS-TS1394 | TS | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
66 | TS-TS1395 | TS | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
69 | TS-TS1396 | TS | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
72 | TS-TS1397 | TS | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
75 | TS-TS1398 | TS | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
78 | TS-TS1399 | TS | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
81 | TS-TS1400 | TS | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZS
19 | TT-AS1001 | TT | AS1001 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE TRANSMITTER | PD-014 | 13 | 390 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
20 | TT-AS1003 | TT | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE TRANSMITTER | PD-014 | 13 | 390 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
21 | TT-AS1015 | TT | AS1015 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER | PD-014 | 13 | 300 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
60 | TT-BH1060-A1 | TT | BH1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
61 | TT-BH1060-A2 | TT | BH1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
62 | TT-BH1060-B1 | TT | BH1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
63 | TT-BH1060-B2 | TT | BH1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
64 | TT-BH1060-C1 | TT | BH1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
65 | TT-BH1060-C2 | TT | BH1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
66 | TT-BH1060-D1 | TT | BH1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
67 | TT-BH1060-D2 | TT | BH1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
71 | TT-BR1020 | TT | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
72 | TT-BR1030 | TT | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
73 | TT-BR1040 | TT | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
74 | TT-BR1110 | TT | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
75 | TT-BR1120-1 | TT | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE TRANSMITTER-1 | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
76 | TT-BR1120-2 | TT | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE TRANSMITTER-2 | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
77 | TT-BR1130-1 | TT | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
78 | TT-BR1130-2 | TT | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
79 | TT-BR1140-1 | TT | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
80 | TT-BR1140-2 | TT | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
81 | TT-BR1150-1 | TT | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
82 | TT-BR1150-2 | TT | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
24 | TT-CD1101 | TT | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
25 | TT-CD1102 | TT | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
26 | TT-CD1103-1 | TT | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
27 | TT-CD1103-2 | TT | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
28 | TT-CD1104 | TT | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE TRANSMITTER | PD-016 | 8 | 170 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
29 | TT-CD1110-1 | TT | CD1110-1 | #1 CONDENSER HOT WELL WATER TEMPERATURE TRANSMITTER-1 | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
30 | TT-CD1110-2 | TT | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE TRANSMITTER-2 | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
31 | TT-CD1110-3 | TT | CD1110-3 | #1 CONDENSER NECK TEMPERATURE TRANSMITTER | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
32 | TT-CD1110-4 | TT | CD1110-4 | #1 CONDENSER FLASH CHAMBERTEMPERATURE TRANSMITTER | PD-016 | 1.03 & Full Vacuum | 120 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
33 | TT-CD1116-A1 | TT | CD1116-A1 | #1 CONDENSAT PUMP (A) COUPLING TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
34 | TT-CD1116-A3 | TT | CD1116-A3 | #1 CONDENSAT PUMP (A) MOTOR BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
35 | TT-CD1116-A4 | TT | CD1116-A4 | #1 CONDENSAT PUMP (A) MOTOR BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
36 | TT-CD1116-AU | TT | CD1116-AU | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
37 | TT-CD1116-AV | TT | CD1116-AV | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
38 | TT-CD1116-AW | TT | CD1116-AW | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
39 | TT-CD1116-B1 | TT | CD1116-B1 | #1 CONDENSAT PUMP (B) COUPLING TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
40 | TT-CD1116-B3 | TT | CD1116-B3 | #1 CONDENSAT PUMP (B) MOTOR BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
41 | TT-CD1116-B4 | TT | CD1116-B4 | #1 CONDENSAT PUMP (B) MOTOR BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
42 | TT-CD1116-BU | TT | CD1116-BU | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
43 | TT-CD1116-BV | TT | CD1116-BV | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
44 | TT-CD1116-BW | TT | CD1116-BW | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
45 | TT-CD1118 | TT | CD1118 | #1 CONDENSATE WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
46 | TT-CD1119 | TT | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
47 | TT-CD1120 | TT | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
48 | TT-CD1122 | TT | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
6 | TT-CR1004 | TT | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE TRANSMITTER | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
7 | TT-CR1005-1 | TT | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
8 | TT-CR1005-2 | TT | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
68 | TT-CW1060-A1 | TT | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
69 | TT-CW1060-A2 | TT | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
70 | TT-CW1060-B1 | TT | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
71 | TT-CW1060-B2 | TT | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
72 | TT-CW1060-C1 | TT | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
73 | TT-CW1060-C2 | TT | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
74 | TT-CW1060-D1 | TT | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
75 | TT-CW1060-D2 | TT | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
103 | TT-CW1108-A3 | TT | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
104 | TT-CW1108-A4 | TT | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR REAR BEARING TEMPERATURE TRANSMITTER-2 | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
105 | TT-CW1108-AU | TT | CW1108-AU | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
106 | TT-CW1108-AV | TT | CW1108-AV | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
107 | TT-CW1108-AW | TT | CW1108-AW | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
108 | TT-CW1108-B3 | TT | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
109 | TT-CW1108-B4 | TT | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
110 | TT-CW1108-BU | TT | CW1108-BU | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
111 | TT-CW1108-BV | TT | CW1108-BV | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
112 | TT-CW1108-BW | TT | CW1108-BW | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
113 | TT-CW1152 | TT | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE TRANSMITTER | PD-021 | 10 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
114 | TT-CW1153 | TT | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE TRANSMITTER | PD-021 | 10 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
2 | TT-CW1156 | TT | CW1156 | #1 AUXILIARY COOLING WATER TEMPERATURE AT BOTTOM ASH SCREW CONVEYOR COMMON HEADER | PD-021 | - | - | 0~150℃ | AI 4~20mA | FIELD | DCS | SMART | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
18 | TT-FA1052-6 | TT | FA1052-6 | #1 AIR PRE-HEATER TOP BEARING TEMPERATUTRE TRANSMITTER | - | - | - | 0~150℃ | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
19 | TT-FA1052-7 | TT | FA1052-7 | #1 AIR PRE-HEATER BOOTOM BEARING TEMPERATUTRE TRANSMITTER | - | - | - | 0~150℃ | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
167 | TT-FA1053-1 | TT | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
168 | TT-FA1053-2 | TT | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
169 | TT-FA1053-3 | TT | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
170 | TT-FA1053-4 | TT | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
171 | TT-FA1053-U | TT | FA1053-U | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
172 | TT-FA1053-V | TT | FA1053-V | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
173 | TT-FA1053-W | TT | FA1053-W | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
179 | TT-FA1054-1 | TT | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
180 | TT-FA1054-2 | TT | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
181 | TT-FA1054-3 | TT | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
182 | TT-FA1054-4 | TT | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
183 | TT-FA1054-U | TT | FA1054-U | #1 SECONDARY AIR FAN MOTOR WINRING (U) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
184 | TT-FA1054-V | TT | FA1054-V | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
185 | TT-FA1054-W | TT | FA1054-W | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
191 | TT-FA1055-A | TT | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 149 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
192 | TT-FA1055-A1 | TT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
193 | TT-FA1055-A2 | TT | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
194 | TT-FA1055-A3 | TT | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
195 | TT-FA1055-A4 | TT | FA1055-A4 | #1 FLUIDIZING AIR BLOWER (A) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
196 | TT-FA1055-AU | TT | FA1055-AU | #1 FLUIDIZING AIR BLOWER (A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
197 | TT-FA1055-AV | TT | FA1055-AV | #1 FLUIDIZING AIR BLOWER (A )MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
198 | TT-FA1055-AW | TT | FA1055-AW | #1 FLUIDIZING AIR BLOWER (A) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
199 | TT-FA1055-B | TT | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 149 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
200 | TT-FA1055-B1 | TT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
201 | TT-FA1055-B2 | TT | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
202 | TT-FA1055-B3 | TT | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
203 | TT-FA1055-B4 | TT | FA1055-B4 | #1 FLUIDIZING AIR BLOWER (B) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
204 | TT-FA1055-BU | TT | FA1055-BU | #1 FLUIDIZING AIR BLOWER (B) MOTOR WINRING (U) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
205 | TT-FA1055-BV | TT | FA1055-BV | #1 FLUIDIZING AIR BLOWER (B )MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
206 | TT-FA1055-BW | TT | FA1055-BW | #1 FLUIDIZING AIR BLOWER (B) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
174 | TT-FA1072 | TT | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE TRANSMITTER | PD-052 | 0 | 66 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
175 | TT-FA1073 | TT | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE (A) TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
176 | TT-FA1074 | TT | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE (B) TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
177 | TT-FA1076 | TT | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE (A) TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
178 | TT-FA1077 | TT | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE (B) TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
186 | TT-FA1082 | TT | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE TRANSMITTER TRANSMITTER | PD-053 | 0 | 66 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
187 | TT-FA1083 | TT | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE (A) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
188 | TT-FA1084 | TT | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE (B) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
189 | TT-FA1086 | TT | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE (A) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
190 | TT-FA1087 | TT | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE (B) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
115 | TT-FG1009-A | TT | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE TEMPERATURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
116 | TT-FG1009-B | TT | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE TEMPERATURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
117 | TT-FG1056-1 | TT | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
118 | TT-FG1056-2 | TT | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
119 | TT-FG1056-3 | TT | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
120 | TT-FG1056-4 | TT | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
121 | TT-FG1056-U | TT | FG1056-U | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
122 | TT-FG1056-V | TT | FG1056-V | #1 INDUCED DRAFT FAN MOTOR WINDIING (V) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
123 | TT-FG1056-W | TT | FG1056-W | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
124 | TT-FG1057-8 | TT | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | 33 mmH2O | 200 | 0~300 | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | TT
125 | TT-FG1090-A | TT | FG1090-A | #1 FURNACE FRONT TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
126 | TT-FG1090-B | TT | FG1090-B | #1 FURNACE FRONT TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
127 | TT-FG1090-C | TT | FG1090-C | #1 FURNACE FRONT TEMPERATURE (C) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
128 | TT-FG1090-D | TT | FG1090-D | #1 FURNACE FRONT TEMPERATURE (D) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
129 | TT-FG1090-E | TT | FG1090-E | #1 FURNACE FRONT TEMPERATURE (E) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
130 | TT-FG1090-F | TT | FG1090-F | #1 FURNACE FRONT TEMPERATURE (F) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
131 | TT-FG1090-G | TT | FG1090-G | #1 FURNACE REAR TEMPERATURE (G) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
132 | TT-FG1090-H | TT | FG1090-H | #1 FURNACE REAR TEMPERATURE (H) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
133 | TT-FG1090-I | TT | FG1090-I | #1 FURNACE REAR TEMPERATURE (I) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
134 | TT-FG1091-A | TT | FG1091-A | #1 FURNACE FRONT TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
135 | TT-FG1091-B | TT | FG1091-B | #1 FURNACE FRONT TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
136 | TT-FG1091-C | TT | FG1091-C | #1 FURNACE FRONT TEMPERATURE (C) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
137 | TT-FG1091-D | TT | FG1091-D | #1 FURNACE FRONT TEMPERATURE (D) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
138 | TT-FG1091-E | TT | FG1091-E | #1 FURNACE FRONT TEMPERATURE (E) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
139 | TT-FG1091-F | TT | FG1091-F | #1 FURNACE FRONT TEMPERATURE (F) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
140 | TT-FG1091-G | TT | FG1091-G | #1 FURNACE REAR TEMPERATURE (G) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
141 | TT-FG1091-H | TT | FG1091-H | #1 FURNACE REAR TEMPERATURE (H) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
142 | TT-FG1091-I | TT | FG1091-I | #1 FURNACE REAR TEMPERATURE (I) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
143 | TT-FG1092-A | TT | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
144 | TT-FG1092-B | TT | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
145 | TT-FG1095-A | TT | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE-1 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
146 | TT-FG1095-B | TT | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE-1 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
147 | TT-FG1096-A | TT | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE-2 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
148 | TT-FG1096-B | TT | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE-2 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
149 | TT-FG1100 | TT | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 900 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
150 | TT-FG1101 | TT | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 900 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
151 | TT-FG1102 | TT | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 700 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
152 | TT-FG1103 | TT | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 700 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
153 | TT-FG1104 | TT | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 600 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
154 | TT-FG1105 | TT | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 620 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
155 | TT-FG1106 | TT | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 520 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
156 | TT-FG1107 | TT | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 590 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
157 | TT-FG1108 | TT | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 480 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
158 | TT-FG1109 | TT | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 520 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
159 | TT-FG1110 | TT | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 430 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
160 | TT-FG1111 | TT | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 450 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
161 | TT-FG1113 | TT | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 430 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
162 | TT-FG1124 | TT | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
163 | TT-FG1125 | TT | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
164 | TT-FG1132 | TT | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
165 | TT-FG1133 | TT | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
166 | TT-FG1152 | TT | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
49 | TT-FW1010 | TT | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 10 | 180 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
50 | TT-FW1011 | TT | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 180 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
51 | TT-FW1105 | TT | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 220 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
52 | TT-FW1106 | TT | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 275 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
53 | TT-FW1115-A1 | TT | FW1115-A1 | #1 BFP(A) PUMP SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
54 | TT-FW1115-A2 | TT | FW1115-A2 | #1 BFP(A) PUMP SIDE BEARING FRONT(DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
55 | TT-FW1115-A3 | TT | FW1115-A3 | #1 BFP(A) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
56 | TT-FW1115-A4 | TT | FW1115-A4 | #1 BFP(A) MOTOR SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
57 | TT-FW1115-AU | TT | FW1115-AU | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
58 | TT-FW1115-AV | TT | FW1115-AV | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
59 | TT-FW1115-AW | TT | FW1115-AW | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
60 | TT-FW1115-B1 | TT | FW1115-B1 | #1 BFP(B) PUMP SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
61 | TT-FW1115-B2 | TT | FW1115-B2 | #1 BFP(B) PUMP SIDE BEARING FRONT(DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
62 | TT-FW1115-B3 | TT | FW1115-B3 | #1 BFP(B) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
63 | TT-FW1115-B4 | TT | FW1115-B4 | #1 BFP(B) MOTOR SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
64 | TT-FW1115-BU | TT | FW1115-BU | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
65 | TT-FW1115-BV | TT | FW1115-BV | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
66 | TT-FW1115-BW | TT | FW1115-BW | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
83 | TT-FW1160 | TT | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 230 | 275 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
67 | TT-HD1102 | TT | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
68 | TT-HD1103 | TT | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
69 | TT-HD1105 | TT | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 16 & Full Vaccum | 210 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
70 | TT-HD1106 | TT | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 45 & Full Vaccum | 260 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
9 | TT-HR1002-1 | TT | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
10 | TT-HR1002-2 | TT | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
11 | TT-HR1004 | TT | HR1004 | #1 REHEAT STEAM TEMPERATURE TRANSMITTER | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
12 | TT-HR1012-1 | TT | HR1012-1 | #1 LOW PRESSURE TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 15 | 280 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
13 | TT-HR1012-2 | TT | HR1012-2 | #1 LOW PRESSURE TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 15 | 280 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
1 | TT-MS1004-1 | TT | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE TRANSMITTER-1 | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
2 | TT-MS1004-2 | TT | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE TRANSMITTER-2 | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
3 | TT-MS1007 | TT | MS1007 | #1 MAIN STEAM TEMPERATURE TRANSMITTER | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
4 | TT-MS1022-1 | TT | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-1 | PD-011 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
5 | TT-MS1022-2 | TT | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-2 | PD-011 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
22 | TT-SB1056 | TT | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE TRANSMITTER | PD-015 | 30 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
23 | TT-SB1057 | TT | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE TRANSMITTER | PD-015 | 30 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
84 | TT-SW1110-A1 | TT | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
85 | TT-SW1110-A2 | TT | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
86 | TT-SW1110-B1 | TT | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
87 | TT-SW1110-B2 | TT | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
88 | TT-SW1501-A3 | TT | SW1501-A3 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
89 | TT-SW1501-A4 | TT | SW1501-A4 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
90 | TT-SW1501-AU | TT | SW1501-AU | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
91 | TT-SW1501-AV | TT | SW1501-AV | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
92 | TT-SW1501-AW | TT | SW1501-AW | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
93 | TT-SW1501-B3 | TT | SW1501-B3 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
94 | TT-SW1501-B4 | TT | SW1501-B4 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
95 | TT-SW1501-BU | TT | SW1501-BU | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
96 | TT-SW1501-BV | TT | SW1501-BV | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
97 | TT-SW1501-BW | TT | SW1501-BW | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
98 | TT-SW1501-C3 | TT | SW1501-C3 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
99 | TT-SW1501-C4 | TT | SW1501-C4 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
100 | TT-SW1501-CU | TT | SW1501-CU | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
101 | TT-SW1501-CV | TT | SW1501-CV | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
102 | TT-SW1501-CW | TT | SW1501-CW | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
14 | TT-TS1011 | TT | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE TRANSMITTER | PD-013 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
15 | TT-TS1014 | TT | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE TRANSMITTER | PD-013 | 16 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
16 | TT-TS1018 | TT | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE TRANSMITTER | PD-013 | 6.2 | 380 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
17 | TT-TS1023 | TT | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
18 | TT-TS1027 | TT | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
48 | TW-AS1001 | TW | AS1001 | #1 MAIN STEAM DESUPERHEATING DOWNSTREAM TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
49 | TW-AS1002 | TW | AS1002 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE GAUGE | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
50 | TW-AS1003 | TW | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
51 | TW-AS1015 | TW | AS1015 | #1 GLAND STEAM DESUPERHEATING OUTLET TEMPERATURE ELEMENT | PD-014 | 13 | 300 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
52 | TW-AS1016 | TW | AS1016 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE GAUGE | PD-014 | 13 | 300 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
104 | TW-BR1020 | TW | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
105 | TW-BR1030 | TW | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
106 | TW-BR1040 | TW | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
107 | TW-BR1110 | TW | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
108 | TW-BR1120-1 | TW | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-1 | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
109 | TW-BR1120-2 | TW | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-2 | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
110 | TW-BR1130-1 | TW | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
111 | TW-BR1130-2 | TW | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
112 | TW-BR1140-1 | TW | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
113 | TW-BR1140-2 | TW | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
114 | TW-BR1150-1 | TW | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
115 | TW-BR1150-2 | TW | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
57 | TW-CD1101 | TW | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
58 | TW-CD1102 | TW | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
59 | TW-CD1103-1 | TW | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
60 | TW-CD1103-2 | TW | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
61 | TW-CD1104 | TW | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE ELEMENT | PD-016 | 8 | 170 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
62 | TW-CD1104-1 | TW | CD1104-1 | #1 DEAERATOR TEMPERATURE GAUGE | PD-016 | 8 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
63 | TW-CD1104-2 | TW | CD1104-2 | #1 DEAERATOR STORAGE TANK TEMPERATURE GAUGE | PD-016 | 8 | 170 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
64 | TW-CD1110-1 | TW | CD1110-1 | #1 CONDENSER HOT WELL STEAM TEMPERATURE ELEMENT-1 | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
65 | TW-CD1110-1(G) | TW | CD1110-1(G) | #1 CONDENSER HOT WELL WATER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
66 | TW-CD1110-2 | TW | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE ELEMENT-2 | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
67 | TW-CD1110-2(G) | TW | CD1110-2(G) | #1 CONDENSER FLASH CHAMBER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
68 | TW-CD1110-3 | TW | CD1110-3 | #1 CONDENSER NECK TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
69 | TW-CD1110-4 | TW | CD1110-4 | #1 CONDENSER FLASH CHAMBER TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
70 | TW-CD1118 | TW | CD1118 | #1 CONDENSATE WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
71 | TW-CD1118(G) | TW | CD1118(G) | #1 CONDENSATE WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
72 | TW-CD1119 | TW | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
73 | TW-CD1119(G) | TW | CD1119(G) | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
74 | TW-CD1120 | TW | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
75 | TW-CD1120(G) | TW | CD1120(G) | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
76 | TW-CD1122 | TW | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
77 | TW-CD1603 | TW | CD1603 | #1 TEST WELL AT CONDENSATE PUMP COMMON DISCHARGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0 |  | TW
78 | TW-CD1604 | TW | CD1604 | #1 TEST WELL AT GLAND STEAM CONDENSER OUTLET | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0 |  | TW
79 | TW-CD1605 | TW | CD1605 | #1 TEST WELL AT LOW PRESSURE HEATER NO.1 INLET CONDENSATE SIDE | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0 |  | TW
80 | TW-CD1607 | TW | CD1607 | #1 TEST WELL AT DEAERATOR INLET CONDENSATE-1 | PD-016 | 24 | 200 | - | - | - | - | - | FHI |  | 0 |  | TW
81 | TW-CD1608 | TW | CD1608 | #1 TEST WELL AT DEAERATOR INLET CONDENSATE-2 | PD-016 | 24 | 200 | - | - | - | - | - | FHI |  | 0 |  | TW
19 | TW-CR1004 | TW | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
20 | TW-CR1005-1 | TW | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
21 | TW-CR1005-2 | TW | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
1 | TW-CR1603 | TW | CR1603 | #1 TEST WELL AT COLD REHEAT LINE B | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
2 | TW-CR1605-1 | TW | CR1605-1 | #1 TEST WELL AT COLD REHEATER COMMON HEADER -1 | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
3 | TW-CR1605-2 | TW | CR1605-2 | #1 TEST WELL AT COLD REHEATER COMMON HEADER -2 | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
134 | TW-CW1107-A | TW | CW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
135 | TW-CW1107-B | TW | CW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
136 | TW-CW1107-C | TW | CW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
137 | TW-CW1115-A1 | TW | CW1115-A1 | #1 BFP MOTOR P-1115A COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
138 | TW-CW1115-B1 | TW | CW1115-B1 | #1 BFP MOTOR P-1115B COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
139 | TW-CW1151 | TW | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
140 | TW-CW1152 | TW | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
141 | TW-CW1152 | TW | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
142 | TW-CW1153 | TW | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
143 | TW-CW1154-A1 | TW | CW1154-A1 | #1 STEAM TURBINE LUBE OIL COOLER A INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
144 | TW-CW1154-A2 | TW | CW1154-A2 | #1 STEAM TURBINE LUBE OIL COOLER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
145 | TW-CW1154-B1 | TW | CW1154-B1 | #1 STEAM TURBINE LUBE OIL COOLER B INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
146 | TW-CW1154-B2 | TW | CW1154-B2 | #1 STEAM TURBINE LUBE OIL COOLER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
147 | TW-CW1155-A1 | TW | CW1155-A1 | #1 GENERATOR AIR COOLER A-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
148 | TW-CW1155-A2 | TW | CW1155-A2 | #1 GENERATOR AIR COOLER A-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
149 | TW-CW1155-A3 | TW | CW1155-A3 | #1 GENERATOR AIR COOLER A-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
150 | TW-CW1155-A4 | TW | CW1155-A4 | #1 GENERATOR AIR COOLER A-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
151 | TW-CW1155-B1 | TW | CW1155-B1 | #1 GENERATOR AIR COOLER B-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
152 | TW-CW1155-B2 | TW | CW1155-B2 | #1 GENERATOR AIR COOLER B-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
153 | TW-CW1155-B3 | TW | CW1155-B3 | #1 GENERATOR AIR COOLER B-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
154 | TW-CW1155-B4 | TW | CW1155-B4 | #1 GENERATOR AIR COOLER B-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
155 | TW-CW1155-C1 | TW | CW1155-C1 | #1 GENERATOR AIR COOLER C INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
156 | TW-CW1155-C2 | TW | CW1155-C2 | #1 GENERATOR AIR COOLER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
157 | TW-CW1155-D1 | TW | CW1155-D1 | #1 GENERATOR AIR COOLER D INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
158 | TW-CW1155-D2 | TW | CW1155-D2 | #1 GENERATOR AIR COOLER D OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
159 | TW-DO0003 | TW | DO0003 | DIESEL OIL PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
160 | TW-DO1006 | TW | DO1006 | #1 DIESEL OIL TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
218 | TW-FA1055-A | TW | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
219 | TW-FA1055-B | TW | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
208 | TW-FA1072 | TW | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-052 | 0 | 66 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
209 | TW-FA1073 | TW | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
210 | TW-FA1074 | TW | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-052 | -340~2500 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
211 | TW-FA1076 | TW | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
212 | TW-FA1077 | TW | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-052 | -340~2500 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
213 | TW-FA1082 | TW | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-053 | 0 | 66 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
214 | TW-FA1083 | TW | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
215 | TW-FA1084 | TW | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
216 | TW-FA1086 | TW | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
217 | TW-FA1087 | TW | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
163 | TW-FG1009-A | TW | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
164 | TW-FG1009-B | TW | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
165 | TW-FG1057-8 | TW | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | PACKAGE (CEMS) | NEW ADDED | 0 |  | TW
166 | TW-FG1090-A | TW | FG1090-A | #1 FURNACE FRONT TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
167 | TW-FG1090-B | TW | FG1090-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
168 | TW-FG1090-C | TW | FG1090-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
169 | TW-FG1090-D | TW | FG1090-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
170 | TW-FG1090-E | TW | FG1090-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
171 | TW-FG1090-F | TW | FG1090-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
172 | TW-FG1090-G | TW | FG1090-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
173 | TW-FG1090-H | TW | FG1090-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
174 | TW-FG1090-I | TW | FG1090-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
175 | TW-FG1091-A | TW | FG1091-A | #1 FURNACE FRONT TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
176 | TW-FG1091-B | TW | FG1091-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
177 | TW-FG1091-C | TW | FG1091-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
178 | TW-FG1091-D | TW | FG1091-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
179 | TW-FG1091-E | TW | FG1091-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
180 | TW-FG1091-F | TW | FG1091-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
181 | TW-FG1091-G | TW | FG1091-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
182 | TW-FG1091-H | TW | FG1091-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
183 | TW-FG1091-I | TW | FG1091-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
184 | TW-FG1092-A | TW | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
185 | TW-FG1092-B | TW | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
186 | TW-FG1095-A | TW | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
187 | TW-FG1095-B | TW | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
188 | TW-FG1096-A | TW | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
189 | TW-FG1096-B | TW | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
190 | TW-FG1100 | TW | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
191 | TW-FG1101 | TW | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
192 | TW-FG1102 | TW | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
193 | TW-FG1103 | TW | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
194 | TW-FG1104 | TW | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 600 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
195 | TW-FG1105 | TW | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 620 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
196 | TW-FG1106 | TW | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
197 | TW-FG1107 | TW | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 590 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
198 | TW-FG1108 | TW | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 480 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
199 | TW-FG1109 | TW | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
200 | TW-FG1110 | TW | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE ELEMENT-A | PD-051 | ±890mmH2O | 430 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
201 | TW-FG1111 | TW | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 450 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
202 | TW-FG1113 | TW | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE ELEMENT-B | PD-051 | ±890mmH2O | 430 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
203 | TW-FG1124 | TW | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 371 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
204 | TW-FG1125 | TW | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(B) | PD-051 | ±890mmH2O | 371 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
205 | TW-FG1132 | TW | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
206 | TW-FG1133 | TW | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
207 | TW-FG1152 | TW | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
82 | TW-FW1010 | TW | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 10 | 180 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
83 | TW-FW1011 | TW | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE ELEMENT | PD-017 | 230 | 180 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
84 | TW-FW1105 | TW | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 220 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
85 | TW-FW1106 | TW | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
116 | TW-FW1160 | TW | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
117 | TW-FW1160(G) | TW | FW1160(G) | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE GAUGE | PD-019 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
86 | TW-FW1601 | TW | FW1601 | #1 TEST WELL AT BFP INLET | PD-017 | 10 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
87 | TW-FW1602 | TW | FW1602 | #1 TEST WELL AT BFP INLET | PD-017 | 10 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
88 | TW-FW1604 | TW | FW1604 | #1 TEST WELL AT BFP COMMON DISCHARGE | PD-017 | 230 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
89 | TW-FW1605 | TW | FW1605 | #1 TEST WELL AT BFP COMMON DISCHARGE | PD-017 | 230 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
90 | TW-FW1606 | TW | FW1606 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER | PD-017 | 230 | 220 | - | - | - | - | - | FHI |  | 0 |  | TW
91 | TW-FW1607 | TW | FW1607 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER | PD-017 | 230 | 220 | - | - | - | - | - | FHI |  | 0 |  | TW
92 | TW-FW1609 | TW | FW1609 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER | PD-017 | 230 | 275 | - | - | - | - | - | FHI |  | 0 |  | TW
93 | TW-FW1610 | TW | FW1610 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER | PD-017 | 230 | 275 | - | - | - | - | - | FHI |  | 0 |  | TW
94 | TW-HD1102 | TW | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
95 | TW-HD1102(G) | TW | HD1102(G) | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
96 | TW-HD1103 | TW | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
97 | TW-HD1103(G) | TW | HD1103(G) | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
98 | TW-HD1105 | TW | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE ELEMENT | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
99 | TW-HD1105(G) | TW | HD1105(G) | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
100 | TW-HD1106 | TW | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
101 | TW-HD1106(G) | TW | HD1106(G) | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
102 | TW-HD1601 | TW | HD1601 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 DRAIN LINE | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI |  | 0 |  | TW
103 | TW-HD1602 | TW | HD1602 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 DRAIN LINE | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI |  | 0 |  | TW
22 | TW-HR1002-1 | TW | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
23 | TW-HR1002-2 | TW | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
24 | TW-HR1004 | TW | HR1004 | #1 REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
25 | TW-HR1010 | TW | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OUTLET TEMPERATURE ELEMENT | PD-012 | - | - | - | - | - | - | - | PACKAGE (CV) | NEW ADDED | 0 |  | TW
26 | TW-HR1012-1 | TW | HR1012-1 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 15 | 280 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
27 | TW-HR1012-2 | TW | HR1012-2 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 15 | 280 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
28 | TW-HR1603-1 | TW | HR1603-1 | #1 TEST WELL AT HOT REHEATER COMMON -1 | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
29 | TW-HR1603-2 | TW | HR1603-2 | #1 TEST WELL AT HOT REHEATER COMMON -2 | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
30 | TW-HR1605 | TW | HR1605 | #1 TEST WELL AT ILP TURBINE LEADING LINE A | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
31 | TW-HR1607 | TW | HR1607 | #1 TEST WELL AT ILP TURBINE LEADING LINE B | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
32 | TW-HR1608 | TW | HR1608 | #1 TEST WELL AT LP TURBINE BYPASS OUTLET | PD-012 | 15 | 280 | - | - | - | - | - | FHI |  | 0 |  | TW
33 | TW-HR1902 | TW | HR1902 | #1 HOT REHEAT STEAM TEMPERATURE | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
34 | TW-HR1902 | TW | HR1902 | #1 THERMOWELL WELL FOR TE-MS1902 AT ILP TURBINE LEADING LINE A | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
162 | TW-IA0151 | TW | IA0151 | IA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-2/6 | 10 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
4 | TW-MS1004-1 | TW | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
5 | TW-MS1004-2 | TW | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
6 | TW-MS1005 | TW | MS1005 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE GAUGE | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
7 | TW-MS1007 | TW | MS1007 | #1 MAIN STEAM TEMPERATURE ELEMENT | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
8 | TW-MS1022-1 | TW | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-011 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
9 | TW-MS1022-2 | TW | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-011 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
10 | TW-MS1602-1 | TW | MS1602-1 | #1 TEST WELL AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
11 | TW-MS1602-2 | TW | MS1602-2 | #1 TEST WELL AT MAIN STEAM LINE-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
12 | TW-MS1604 | TW | MS1604 | #1 TEST WELL AT TURBINE LEADING LINE A | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
13 | TW-MS1606 | TW | MS1606 | #1 TEST WELL AT TURBINE LEADING LINE B | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
14 | TW-MS1607 | TW | MS1607 | #1 TEST WELL AT HP TURBINE BYPASS OUTLET | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
15 | TW-MS1902-1 | TW | MS1902-1 | #1 THERMOWELL WELL FOR TE-MS1902-1 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
16 | TW-MS1902-2 | TW | MS1902-2 | #1 THERMOWELL WELL FOR TE-MS1902-2 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
17 | TW-MS1902-3 | TW | MS1902-3 | #1 THERMOWELL WELL FOR TE-MS1902-3 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
18 | TW-MS1902-4 | TW | MS1902-4 | #1 THERMOWELL WELL FOR TE-MS1902-4 AT MAIN INLET STEAM LINE-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
161 | TW-PA0151 | TW | PA0151 | PA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-1/6 | 10 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
53 | TW-SB1055 | TW | SB1055 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
54 | TW-SB1056 | TW | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
55 | TW-SB1057 | TW | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
56 | TW-SB1058 | TW | SB1058 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
118 | TW-SW1107-A | TW | SW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
119 | TW-SW1107-B | TW | SW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
120 | TW-SW1107-C | TW | SW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
121 | TW-SW1110-A1 | TW | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
122 | TW-SW1110-A1(G) | TW | SW1110-A1(G) | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
123 | TW-SW1110-A2 | TW | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
124 | TW-SW1110-A2(G) | TW | SW1110-A2(G) | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
125 | TW-SW1110-B1 | TW | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
126 | TW-SW1110-B1(G) | TW | SW1110-B1(G) | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
127 | TW-SW1110-B2 | TW | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
128 | TW-SW1110-B2(G) | TW | SW1110-B2(G) | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
129 | TW-SW1503-A | TW | SW1503-A | #1 SEAWATER BOOSTER PUMP A SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
130 | TW-SW1503-B | TW | SW1503-B | #1 SEAWATER BOOSTER PUMP B SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
131 | TW-SW1503-C | TW | SW1503-C | #1 SEAWATER BOOSTER PUMP C SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
132 | TW-SW1551 | TW | SW1551 | #1 SEAWATER PUMP DISCHARGE HEADER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
133 | TW-SW1552 | TW | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
35 | TW-TS1011 | TW | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-013 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
36 | TW-TS1012 | TW | TS1012 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE GAUGE | PD-013 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
37 | TW-TS1014 | TW | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE ELEMENT | PD-013 | 16 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
38 | TW-TS1016 | TW | TS1016 | #1 EXTRACTION STEAM NO.2 TEMPERATURE GAUGE | PD-013 | 16 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
39 | TW-TS1018 | TW | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE ELEMENT | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
40 | TW-TS1021 | TW | TS1021 | #1 DEAERATOR INLET STEAM TEMPERATURE GAUGE | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
41 | TW-TS1023 | TW | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
42 | TW-TS1025 | TW | TS1025 | #1 EXTRACTION STEAM NO.4 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
43 | TW-TS1027 | TW | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
44 | TW-TS1029 | TW | TS1029 | #1 EXTRACTION STEAM NO.5 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
45 | TW-TS1602 | TW | TS1602 | #1 TEST WELL AT COLD REHEATER TO #2 HIGH PRESSURE HEATER | PD-013 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
46 | TW-TS1604 | TW | TS1604 | #1 TEST WELL AT EXTRACTION STEAM NO.2 LINE | PD-013 | 16 | 440 | - | - | - | - | - | FHI |  | 0 |  | TW
47 | TW-TS1606 | TW | TS1606 | #1 TEST WELL AT EXTRACTION STEAM NO.3 LINE | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI |  | 0 |  | TW
1 | VT-CD1116-A1 | VT | CD1116-A1 | #1 CONDENSATE PUMP (A) VIBRATION TRANSMITTER-1 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
2 | VT-CD1116-A2 | VT | CD1116-A2 | #1 CONDENSATE PUMP (A) VIBRATION TRANSMITTER-2 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
3 | VT-CD1116-A3 | VT | CD1116-A3 | #1 CONDENSATE PUMP (A) MOTOR DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
4 | VT-CD1116-A4 | VT | CD1116-A4 | #1 CONDENSATE PUMP (A) MOTOR NON-DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
5 | VT-CD1116-B1 | VT | CD1116-B1 | #1 CONDENSATE PUMP (B) VIBRATION TRANSMITTER-1 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
6 | VT-CD1116-B2 | VT | CD1116-B2 | #1 CONDENSATE PUMP (B) VIBRATION TRANSMITTER-2 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
7 | VT-CD1116-B3 | VT | CD1116-B3 | #1 CONDENSATE PUMP (B) MOTOR DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
8 | VT-CD1116-B4 | VT | CD1116-B4 | #1 CONDENSATE PUMP (B) MOTOR NON-DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
31 | VT-CW1108-A3 | VT | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
32 | VT-CW1108-A4 | VT | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
33 | VT-CW1108-B3 | VT | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
34 | VT-CW1108-B4 | VT | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
13 | VT-FA1053-1 | VT | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
14 | VT-FA1053-2 | VT | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
15 | VT-FA1053-3 | VT | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
16 | VT-FA1053-4 | VT | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
57 | VT-FA1054-1 | VT | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
58 | VT-FA1054-2 | VT | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
59 | VT-FA1054-3 | VT | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
60 | VT-FA1054-4 | VT | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
35 | VT-FA1055-A1 | VT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) REAR BEARING VIBRATION TRANSMITTER-1 | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
36 | VT-FA1055-A2 | VT | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
37 | VT-FA1055-A3 | VT | FA1055-A3 | #1 FLUIDIZING AIR BLOWER(A) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
38 | VT-FA1055-A4 | VT | FA1055-A4 | #1 FLUIDIZING AIR BLOWER(A) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
39 | VT-FA1055-B1 | VT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) REAR BEARING VIBRATION TRANSMITTER-1 | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
40 | VT-FA1055-B2 | VT | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
41 | VT-FA1055-B3 | VT | FA1055-B3 | #1 FLUIDIZING AIR BLOWER(B) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
42 | VT-FA1055-B4 | VT | FA1055-B4 | #1 FLUIDIZING AIR BLOWER(B) MOTOR RAER BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
26 | VT-FG1056-1 | VT | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
27 | VT-FG1056-2 | VT | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
28 | VT-FG1056-3 | VT | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
29 | VT-FG1056-4 | VT | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
9 | VT-FW1115-A11 | VT | FW1115-A11 | #1 BFP(A) PUMP CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
10 | VT-FW1115-A12 | VT | FW1115-A12 | #1 BFP(A) PUMP CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
11 | VT-FW1115-A21 | VT | FW1115-A21 | #1 BFP(A) PUMP CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
12 | VT-FW1115-A22 | VT | FW1115-A22 | #1 BFP(A) PUMP CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
13 | VT-FW1115-A31 | VT | FW1115-A31 | #1 BFP(A) MOTOR CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
14 | VT-FW1115-A32 | VT | FW1115-A32 | #1 BFP(A) MOTOR CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
15 | VT-FW1115-A41 | VT | FW1115-A41 | #1 BFP(A) MOTOR CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
16 | VT-FW1115-A42 | VT | FW1115-A42 | #1 BFP(A) MOTOR CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
17 | VT-FW1115-B11 | VT | FW1115-B11 | #1 BFP(B) PUMP CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
18 | VT-FW1115-B12 | VT | FW1115-B12 | #1 BFP(B) PUMP CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
19 | VT-FW1115-B21 | VT | FW1115-B21 | #1 BFP(B) PUMP CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
20 | VT-FW1115-B22 | VT | FW1115-B22 | #1 BFP(B) PUMP CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
21 | VT-FW1115-B31 | VT | FW1115-B31 | #1 BFP(B) MOTOR CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
22 | VT-FW1115-B32 | VT | FW1115-B32 | #1 BFP(B) MOTOR CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
23 | VT-FW1115-B41 | VT | FW1115-B41 | #1 BFP(B) MOTOR CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
24 | VT-FW1115-B42 | VT | FW1115-B42 | #1 BFP(B) MOTOR CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
25 | VT-SW1501-A1 | VT | SW1501-A1 | #1 SEWATER PUMP (A) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
26 | VT-SW1501-A2 | VT | SW1501-A2 | #1 SEWATER PUMP (A) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
27 | VT-SW1501-B1 | VT | SW1501-B1 | #1 SEWATER PUMP (B) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
28 | VT-SW1501-B2 | VT | SW1501-B2 | #1 SEWATER PUMP (B) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
29 | VT-SW1501-C1 | VT | SW1501-C1 | #1 SEWATER PUMP (C) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
30 | VT-SW1501-C2 | VT | SW1501-C2 | #1 SEWATER PUMP (C) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
37 | WT-CL1061-A1 | WT | CL1061-A1 | #1 A-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
38 | WT-CL1061-A2 | WT | CL1061-A2 | #1 A-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
39 | WT-CL1061-B1 | WT | CL1061-B1 | #1 B-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
40 | WT-CL1061-B2 | WT | CL1061-B2 | #1 B-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
41 | WT-CL1061-C1 | WT | CL1061-C1 | #1 C-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
42 | WT-CL1061-C2 | WT | CL1061-C2 | #1 C-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
10 | XV-CD1004 | XV | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
11 | XV-CD1005 | XV | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
12 | XV-CD1006 | XV | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
13 | XV-CD1104-2 | XV | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER | PD-016 | 8 | 170 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
14 | XV-CD1114 | XV | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
15 | XV-CD1123 | XV | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
16 | XV-CD1125 | XV | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
43 | XV-CL1061-A7 | XV | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
44 | XV-CL1061-B7 | XV | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
45 | XV-CL1061-C7 | XV | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
1 | XV-CR1011 | XV | CR1011 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 DRAIN VALVE | PD-011 | 45 | 395 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
2 | XV-CR1012 | XV | CR1012 | #1 COLD REHEATER LINE B DRAIN POT DP-CR02 DRAIN VALVE | PD-011 | 45 | 395 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
24 | XV-DO1043-A1 | XV | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
25 | XV-DO1043-A2 | XV | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
70 | XV-DO1043-B1 | XV | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
71 | XV-DO1043-B2 | XV | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
116 | XV-DO1043-C1 | XV | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
117 | XV-DO1043-C2 | XV | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
162 | XV-DO1043-D1 | XV | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
163 | XV-DO1043-D2 | XV | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
43 | XV-FA1055-A2 | XV | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
44 | XV-FA1055-A3 | XV | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
45 | XV-FA1055-B2 | XV | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
46 | XV-FA1055-B3 | XV | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
24 | XV-FS1005 | XV | FS1005 | #1 FLASH PIPE DRAIN VALVE | PD-027 | 8 | 280 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
17 | XV-FW1061 | XV | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 100 | 180 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
18 | XV-FW1111-1 | XV | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
19 | XV-FW1111-2 | XV | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
20 | XV-FW1121-1 | XV | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
21 | XV-FW1121-2 | XV | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
22 | XV-FW1151 | XV | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 100 | 180 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
5 | XV-HR1010-1 | XV | HR1010-1 | #1 LP TURBINE BYPASS VALVE WARMING VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
6 | XV-HR1021 | XV | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
7 | XV-HR1022 | XV | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
3 | XV-MS1011 | XV | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE | PD-011 | 144 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
4 | XV-MS1023 | XV | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE | PD-011 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
23 | XV-MU1109 | XV | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE | PD-021 | 10 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
26 | XV-PA1043-A2 | XV | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
27 | XV-PA1043-A3 | XV | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
72 | XV-PA1043-B2 | XV | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
73 | XV-PA1043-B3 | XV | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
118 | XV-PA1043-C2 | XV | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
119 | XV-PA1043-C3 | XV | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
164 | XV-PA1043-D2 | XV | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
165 | XV-PA1043-D3 | XV | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
8 | XV-SB1054 | XV | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE | PD-015 | 30 | 360 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
9 | XV-SB1059 | XV | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE | PD-015 | 30 | 360 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
29 | ZS1-FA1043-A | ZS1 | FA1043-A | #1 BURNER(A) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
75 | ZS1-FA1043-B | ZS1 | FA1043-B | #1 BURNER(B) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
121 | ZS1-FA1043-C | ZS1 | FA1043-C | #1 BURNER(C) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
167 | ZS1-FA1043-D | ZS1 | FA1043-D | #1 BURNER(D) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
30 | ZS2-FA1043-A | ZS2 | FA1043-A | #1 BURNER(A) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
76 | ZS2-FA1043-B | ZS2 | FA1043-B | #1 BURNER(B) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
122 | ZS2-FA1043-C | ZS2 | FA1043-C | #1 BURNER(C) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
168 | ZS2-FA1043-D | ZS2 | FA1043-D | #1 BURNER(D) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
82 | ZSC-AS1010 | ZSC | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
84 | ZSC-AS1391 | ZSC | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
87 | ZSC-AS1392 | ZSC | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
90 | ZSC-AS1393 | ZSC | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
1 | ZSC-AS1394 | ZSC | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
93 | ZSC-AS1395 | ZSC | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
96 | ZSC-AS1396 | ZSC | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
206 | ZSC-AV1391 | ZSC | AV1391 | #1 CONDENSER VACUUM BREAKER MOV CLOSE POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
174 | ZSC-BD1001 | ZSC | BD1001 | #1 BOILER MASS BLOWDOWN MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
177 | ZSC-BD1002 | ZSC | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
180 | ZSC-BR1391 | ZSC | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
106 | ZSC-CD1001 | ZSC | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
108 | ZSC-CD1001 | ZSC | CD1001 | #1 LP HEATER NO.1 INLET CONDENSATE SHUT-OFF MOV CLOSE POSITION TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
109 | ZSC-CD1002 | ZSC | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
112 | ZSC-CD1003 | ZSC | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
115 | ZSC-CD1004 | ZSC | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
117 | ZSC-CD1005 | ZSC | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
119 | ZSC-CD1006 | ZSC | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
121 | ZSC-CD1007 | ZSC | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
124 | ZSC-CD1008 | ZSC | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
127 | ZSC-CD1104-2 | ZSC | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
142 | ZSC-CD1114 | ZSC | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
129 | ZSC-CD1115 | ZSC | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
131 | ZSC-CD1123 | ZSC | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
133 | ZSC-CD1124 | ZSC | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
135 | ZSC-CD1125 | ZSC | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
137 | ZSC-CD1126 | ZSC | CD1126 | #1 GLAND STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
46 | ZSC-CL1061-A1 | ZSC | CL1061-A1 | #1 A-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
47 | ZSC-CL1061-A2 | ZSC | CL1061-A2 | #1 A-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
48 | ZSC-CL1061-A7 | ZSC | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
49 | ZSC-CL1061-B1 | ZSC | CL1061-B1 | #1 B-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
50 | ZSC-CL1061-B2 | ZSC | CL1061-B2 | #1 B-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
51 | ZSC-CL1061-B7 | ZSC | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
52 | ZSC-CL1061-C1 | ZSC | CL1061-C1 | #1 C-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
53 | ZSC-CL1061-C2 | ZSC | CL1061-C2 | #1 C-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
54 | ZSC-CL1061-C7 | ZSC | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
4 | ZSC-CR1011 | ZSC | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
6 | ZSC-CR1012 | ZSC | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
31 | ZSC-DO1043-A1 | ZSC | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
32 | ZSC-DO1043-A2 | ZSC | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
77 | ZSC-DO1043-B1 | ZSC | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
78 | ZSC-DO1043-B2 | ZSC | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
123 | ZSC-DO1043-C1 | ZSC | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
124 | ZSC-DO1043-C2 | ZSC | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
169 | ZSC-DO1043-D1 | ZSC | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
170 | ZSC-DO1043-D2 | ZSC | DO1043-D2 | #1 BURNER(D) FUEL OILPNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
61 | ZSC-FA1005 | ZSC | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
62 | ZSC-FA1006 | ZSC | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
63 | ZSC-FA1007 | ZSC | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
64 | ZSC-FA1008 | ZSC | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
65 | ZSC-FA1009 | ZSC | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
66 | ZSC-FA1010 | ZSC | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
67 | ZSC-FA1011 | ZSC | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
68 | ZSC-FA1012 | ZSC | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
69 | ZSC-FA1013 | ZSC | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
70 | ZSC-FA1014 | ZSC | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
71 | ZSC-FA1015 | ZSC | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
72 | ZSC-FA1016 | ZSC | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
73 | ZSC-FA1017 | ZSC | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
74 | ZSC-FA1018 | ZSC | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
75 | ZSC-FA1019 | ZSC | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
76 | ZSC-FA1020 | ZSC | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
77 | ZSC-FA1021 | ZSC | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
78 | ZSC-FA1022 | ZSC | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
79 | ZSC-FA1023 | ZSC | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
80 | ZSC-FA1024 | ZSC | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
81 | ZSC-FA1025 | ZSC | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
82 | ZSC-FA1026 | ZSC | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
33 | ZSC-FA1043-A | ZSC | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
79 | ZSC-FA1043-B | ZSC | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
125 | ZSC-FA1043-C | ZSC | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
171 | ZSC-FA1043-D | ZSC | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
17 | ZSC-FA1053-1 | ZSC | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
83 | ZSC-FA1054-1 | ZSC | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
47 | ZSC-FA1055-A1 | ZSC | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
48 | ZSC-FA1055-A2 | ZSC | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
49 | ZSC-FA1055-A3 | ZSC | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
50 | ZSC-FA1055-B1 | ZSC | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
51 | ZSC-FA1055-B2 | ZSC | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
52 | ZSC-FA1055-B3 | ZSC | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
30 | ZSC-FG1056-1 | ZSC | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE PNEUMATIC CONTROL DAMPER CLOSE POSITION SWITCH | PD-051 | - | - | - | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
209 | ZSC-FS1005 | ZSC | FS1005 | #1 FLASH PIPE DRAIN VALVE CLOSE POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
144 | ZSC-FW1001 | ZSC | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
147 | ZSC-FW1002 | ZSC | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
152 | ZSC-FW1060 | ZSC | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
154 | ZSC-FW1061 | ZSC | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
156 | ZSC-FW1111-1 | ZSC | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
158 | ZSC-FW1111-2 | ZSC | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
160 | ZSC-FW1121-1 | ZSC | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
162 | ZSC-FW1121-2 | ZSC | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUPCLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
164 | ZSC-FW1150 | ZSC | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
166 | ZSC-FW1151 | ZSC | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
168 | ZSC-FW1391 | ZSC | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
171 | ZSC-FW1392 | ZSC | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
20 | ZSC-HR1010 | ZSC | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE CLOSE POSITION SWITCH | PD-012 | - | - | #VALUE! | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
22 | ZSC-HR1010-1 | ZSC | HR1010-1 | #1 LP TURBINE BYPASS WARMING VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
24 | ZSC-HR1021 | ZSC | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
26 | ZSC-HR1022 | ZSC | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
28 | ZSC-HR1391 | ZSC | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
203 | ZSC-IW0391 | ZSC | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV CLOSE POSITION SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
31 | ZSC-LO1756 | ZSC | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING COUPLING SCOOP TUBE POSITION(0%) | PD-051 | - | - | - | DI | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
8 | ZSC-MS1011 | ZSC | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
10 | ZSC-MS1020 | ZSC | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
12 | ZSC-MS1023 | ZSC | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
14 | ZSC-MS1391 | ZSC | MS1391 | #1 MAIN STEAM SHUT-OFF MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
17 | ZSC-MS1392 | ZSC | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
139 | ZSC-MU1001 | ZSC | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
202 | ZSC-MU1109 | ZSC | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE CLOSE POSITION SWITCH | PD-021 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
34 | ZSC-PA1043-A2 | ZSC | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
35 | ZSC-PA1043-A3 | ZSC | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
80 | ZSC-PA1043-B2 | ZSC | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
81 | ZSC-PA1043-B3 | ZSC | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
126 | ZSC-PA1043-C2 | ZSC | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
127 | ZSC-PA1043-C3 | ZSC | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
172 | ZSC-PA1043-D2 | ZSC | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
173 | ZSC-PA1043-D3 | ZSC | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
99 | ZSC-SB1001 | ZSC | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
102 | ZSC-SB1054 | ZSC | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
104 | ZSC-SB1059 | ZSC | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
183 | ZSC-SW1001 | ZSC | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
186 | ZSC-SW1002 | ZSC | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
189 | ZSC-SW1003 | ZSC | SW1003 | #1 BALL VESSEL T-1116 INLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
192 | ZSC-SW1004 | ZSC | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
195 | ZSC-SW1005 | ZSC | SW1005 | #1 BALL VESSEL T-1115 INLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
198 | ZSC-SW1006 | ZSC | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
31 | ZSC-TS1001 | ZSC | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
34 | ZSC-TS1002 | ZSC | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
37 | ZSC-TS1003 | ZSC | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
40 | ZSC-TS1004 | ZSC | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
42 | ZSC-TS1004 | ZSC | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV CLOSE POSITION TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
43 | ZSC-TS1005 | ZSC | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
46 | ZSC-TS1389 | ZSC | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
49 | ZSC-TS1390 | ZSC | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
52 | ZSC-TS1391 | ZSC | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
55 | ZSC-TS1392 | ZSC | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
58 | ZSC-TS1393 | ZSC | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
61 | ZSC-TS1394 | ZSC | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
64 | ZSC-TS1395 | ZSC | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
67 | ZSC-TS1396 | ZSC | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
70 | ZSC-TS1397 | ZSC | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
73 | ZSC-TS1398 | ZSC | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
76 | ZSC-TS1399 | ZSC | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
79 | ZSC-TS1400 | ZSC | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZS
28 | ZS-DO1043-A3 | ZS | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
74 | ZS-DO1043-B3 | ZS | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
120 | ZS-DO1043-C3 | ZS | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
166 | ZS-DO1043-D3 | ZS | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
36 | ZSE-DO1043-A4 | ZSE | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
37 | ZSE-DO1043-A5 | ZSE | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
82 | ZSE-DO1043-B4 | ZSE | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
83 | ZSE-DO1043-B5 | ZSE | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
128 | ZSE-DO1043-C4 | ZSE | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
129 | ZSE-DO1043-C5 | ZSE | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
174 | ZSE-DO1043-D4 | ZSE | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
175 | ZSE-DO1043-D5 | ZSE | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
20 | ZSF-SB1040 | ZSF | SB1040 | #1 HOT END SOOTBLOWER LANCE EXTEND LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
21 | ZSF-SB1042 | ZSF | SB1042 | #1 COLD END SOOTBLOWER LANCE EXTEND LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
83 | ZSO-AS1010 | ZSO | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
85 | ZSO-AS1391 | ZSO | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
88 | ZSO-AS1392 | ZSO | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
91 | ZSO-AS1393 | ZSO | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
2 | ZSO-AS1394 | ZSO | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
94 | ZSO-AS1395 | ZSO | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
97 | ZSO-AS1396 | ZSO | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
207 | ZSO-AV1391 | ZSO | AV1391 | #1 CONDENSER VACUUM BREAKER MOV OPEN POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
175 | ZSO-BD1001 | ZSO | BD1001 | #1 BOILER MASS BLOWDOWN MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
178 | ZSO-BD1002 | ZSO | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
181 | ZSO-BR1391 | ZSO | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
107 | ZSO-CD1001 | ZSO | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
110 | ZSO-CD1002 | ZSO | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
113 | ZSO-CD1003 | ZSO | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
116 | ZSO-CD1004 | ZSO | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
118 | ZSO-CD1005 | ZSO | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
120 | ZSO-CD1006 | ZSO | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
122 | ZSO-CD1007 | ZSO | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
125 | ZSO-CD1008 | ZSO | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
128 | ZSO-CD1104-2 | ZSO | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
143 | ZSO-CD1114 | ZSO | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
130 | ZSO-CD1115 | ZSO | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
132 | ZSO-CD1123 | ZSO | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
134 | ZSO-CD1124 | ZSO | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
136 | ZSO-CD1125 | ZSO | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
138 | ZSO-CD1126 | ZSO | CD1126 | #1 GLAND STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
55 | ZSO-CL1061-A1 | ZSO | CL1061-A1 | #1 A-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
56 | ZSO-CL1061-A2 | ZSO | CL1061-A2 | #1 A-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
57 | ZSO-CL1061-A7 | ZSO | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
58 | ZSO-CL1061-B1 | ZSO | CL1061-B1 | #1 B-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
59 | ZSO-CL1061-B2 | ZSO | CL1061-B2 | #1 B-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
60 | ZSO-CL1061-B7 | ZSO | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
61 | ZSO-CL1061-C1 | ZSO | CL1061-C1 | #1 C-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
62 | ZSO-CL1061-C2 | ZSO | CL1061-C2 | #1 C-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
63 | ZSO-CL1061-C7 | ZSO | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
5 | ZSO-CR1011 | ZSO | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
7 | ZSO-CR1012 | ZSO | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
38 | ZSO-DO1043-A1 | ZSO | DO1043-A1 | BURNER(A) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
39 | ZSO-DO1043-A2 | ZSO | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
84 | ZSO-DO1043-B1 | ZSO | DO1043-B1 | BURNER(B) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
85 | ZSO-DO1043-B2 | ZSO | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
130 | ZSO-DO1043-C1 | ZSO | DO1043-C1 | BURNER(C) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
131 | ZSO-DO1043-C2 | ZSO | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
176 | ZSO-DO1043-D1 | ZSO | DO1043-D1 | BURNER(D) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
177 | ZSO-DO1043-D2 | ZSO | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
84 | ZSO-FA1005 | ZSO | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
85 | ZSO-FA1006 | ZSO | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
86 | ZSO-FA1007 | ZSO | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
87 | ZSO-FA1008 | ZSO | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
88 | ZSO-FA1009 | ZSO | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
89 | ZSO-FA1010 | ZSO | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
90 | ZSO-FA1011 | ZSO | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
91 | ZSO-FA1012 | ZSO | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
92 | ZSO-FA1013 | ZSO | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
93 | ZSO-FA1014 | ZSO | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
94 | ZSO-FA1015 | ZSO | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
95 | ZSO-FA1016 | ZSO | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
96 | ZSO-FA1017 | ZSO | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
97 | ZSO-FA1018 | ZSO | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
98 | ZSO-FA1019 | ZSO | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
99 | ZSO-FA1020 | ZSO | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
100 | ZSO-FA1021 | ZSO | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
101 | ZSO-FA1022 | ZSO | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
102 | ZSO-FA1023 | ZSO | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
103 | ZSO-FA1024 | ZSO | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
104 | ZSO-FA1025 | ZSO | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
105 | ZSO-FA1026 | ZSO | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
40 | ZSO-FA1043-A | ZSO | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
86 | ZSO-FA1043-B | ZSO | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
132 | ZSO-FA1043-C | ZSO | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
178 | ZSO-FA1043-D | ZSO | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
18 | ZSO-FA1053-1 | ZSO | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
106 | ZSO-FA1054-1 | ZSO | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
53 | ZSO-FA1055-A1 | ZSO | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
54 | ZSO-FA1055-A2 | ZSO | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
55 | ZSO-FA1055-A3 | ZSO | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
56 | ZSO-FA1055-B1 | ZSO | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
57 | ZSO-FA1055-B2 | ZSO | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
58 | ZSO-FA1055-B3 | ZSO | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
32 | ZSO-FG1056-1 | ZSO | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE PNEUMATIC CONTROL DAMPER OPEN POSITION SWITCH | PD-051 | - | - | - | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
210 | ZSO-FS1005 | ZSO | FS1005 | #1 FLASH PIPE DRAIN VALVE OPEN POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
145 | ZSO-FW1001 | ZSO | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
148 | ZSO-FW1002 | ZSO | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
150 | ZSO-FW1031 | ZSO | FW1031 | #1 BFP(A) SUCTION MANUAL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
151 | ZSO-FW1032 | ZSO | FW1032 | #1 BFP(B) SUCTION MANUAL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
153 | ZSO-FW1060 | ZSO | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
155 | ZSO-FW1061 | ZSO | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
157 | ZSO-FW1111-1 | ZSO | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
159 | ZSO-FW1111-2 | ZSO | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
161 | ZSO-FW1121-1 | ZSO | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
163 | ZSO-FW1121-2 | ZSO | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUPOPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
165 | ZSO-FW1150 | ZSO | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
167 | ZSO-FW1151 | ZSO | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
169 | ZSO-FW1391 | ZSO | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
172 | ZSO-FW1392 | ZSO | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
21 | ZSO-HR1010 | ZSO | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
23 | ZSO-HR1010-1 | ZSO | HR1010-1 | #1 LP TURBINE BYPASS WARMING VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
25 | ZSO-HR1021 | ZSO | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
27 | ZSO-HR1022 | ZSO | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
29 | ZSO-HR1391 | ZSO | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
204 | ZSO-IW0391 | ZSO | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV OPEN POSITION SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
33 | ZSO-LO1756 | ZSO | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING SCOOP TUBE POSITION(100%) | PD-051 | - | - | - | DI | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
9 | ZSO-MS1011 | ZSO | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
11 | ZSO-MS1020 | ZSO | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
13 | ZSO-MS1023 | ZSO | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
15 | ZSO-MS1391 | ZSO | MS1391 | #1 MAIN STEAM SHUT-OFF MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
18 | ZSO-MS1392 | ZSO | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
140 | ZSO-MU1001 | ZSO | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
201 | ZSO-MU1109 | ZSO | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE OPEN POSITION SWITCH | PD-021 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
41 | ZSO-PA1043-A2 | ZSO | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
42 | ZSO-PA1043-A3 | ZSO | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
87 | ZSO-PA1043-B2 | ZSO | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
88 | ZSO-PA1043-B3 | ZSO | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
133 | ZSO-PA1043-C2 | ZSO | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
134 | ZSO-PA1043-C3 | ZSO | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
179 | ZSO-PA1043-D2 | ZSO | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
180 | ZSO-PA1043-D3 | ZSO | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
100 | ZSO-SB1001 | ZSO | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
103 | ZSO-SB1054 | ZSO | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
105 | ZSO-SB1059 | ZSO | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
184 | ZSO-SW1001 | ZSO | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
187 | ZSO-SW1002 | ZSO | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
190 | ZSO-SW1003 | ZSO | SW1003 | #1 BALL VESSEL T-1116 INLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
193 | ZSO-SW1004 | ZSO | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
196 | ZSO-SW1005 | ZSO | SW1005 | #1 BALL VESSEL T-1115 INLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
199 | ZSO-SW1006 | ZSO | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
32 | ZSO-TS1001 | ZSO | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
35 | ZSO-TS1002 | ZSO | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
38 | ZSO-TS1003 | ZSO | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
41 | ZSO-TS1004 | ZSO | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
44 | ZSO-TS1005 | ZSO | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
47 | ZSO-TS1389 | ZSO | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
50 | ZSO-TS1390 | ZSO | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
53 | ZSO-TS1391 | ZSO | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
56 | ZSO-TS1392 | ZSO | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
59 | ZSO-TS1393 | ZSO | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
62 | ZSO-TS1394 | ZSO | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
65 | ZSO-TS1395 | ZSO | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
68 | ZSO-TS1396 | ZSO | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
71 | ZSO-TS1397 | ZSO | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
74 | ZSO-TS1398 | ZSO | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
77 | ZSO-TS1399 | ZSO | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
80 | ZSO-TS1400 | ZSO | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZS
43 | ZSR-DO1043-A4 | ZSR | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
44 | ZSR-DO1043-A5 | ZSR | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
89 | ZSR-DO1043-B4 | ZSR | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
90 | ZSR-DO1043-B5 | ZSR | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
135 | ZSR-DO1043-C4 | ZSR | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
136 | ZSR-DO1043-C5 | ZSR | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
181 | ZSR-DO1043-D4 | ZSR | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
182 | ZSR-DO1043-D5 | ZSR | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
22 | ZSR-SB1040 | ZSR | SB1040 | #1 HOT END SOOTBLOWER LANCE PARK LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
23 | ZSR-SB1042 | ZSR | SB1042 | #1 COLD END SOOTBLOWER LANCE PARK LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
25 | ZT-AS1010 | ZT | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
26 | ZT-AS1020-1 | ZT | AS1020-1 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER (LOW LOAD) | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
27 | ZT-AS1020-2 | ZT | AS1020-2 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER (HIGH LOAD) | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
28 | ZT-AS1030 | ZT | AS1030 | #1 DEAERATOR PEGGING STEAM CONTROL VALVE POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
29 | ZT-AS1391 | ZT | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
30 | ZT-AS1392 | ZT | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
31 | ZT-AS1393 | ZT | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
1 | ZT-AS1394 | ZT | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
32 | ZT-AS1395 | ZT | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
33 | ZT-AS1396 | ZT | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
80 | ZT-AV1391 | ZT | AV1391 | #1 CONDENSER VACUUM BREAKER MOV POSITION TRANSMITTER | PD-027 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
72 | ZT-BD1001 | ZT | BD1001 | #1 BOILER MASS BLOWDOWN MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
73 | ZT-BD1002 | ZT | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
74 | ZT-BR1391 | ZT | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
36 | ZT-CD1001 | ZT | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
37 | ZT-CD1002 | ZT | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
38 | ZT-CD1003 | ZT | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
39 | ZT-CD1007 | ZT | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
40 | ZT-CD1008 | ZT | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
41 | ZT-CD1104 | ZT | CD1104 | #1 DEAERATOR LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
42 | ZT-CD1110 | ZT | CD1110 | #1 CONDENSATE DUMPING VALVE TO RAW WATER PIT LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
43 | ZT-CD1115 | ZT | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
44 | ZT-CD1120 | ZT | CD1120 | #1 CONDENSATE SYSTEM MINIMUM FLOW RECIRCULATION CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
45 | ZT-CD1121 | ZT | CD1121 | #1 CONDENSATE POLISHIER FLOW CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
46 | ZT-CD1124 | ZT | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
47 | ZT-CD1126 | ZT | CD1126 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
75 | ZT-CW1201 | ZT | CW1201 | #1 STEAM TURBINE LUBE OIL TEMPERATURE CONTROL VALVE POSITION TRANSMITTER | PD-021 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
76 | ZT-DO0002 | ZT | DO0002 | DIESEL OIL SYSTEM PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
77 | ZT-DO1009 | ZT | DO1009 | #1 DIESEL OIL RETURN PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
78 | ZT-DO1012 | ZT | DO1012 | #1 DIESEL OIL SUPPLY TO BURNER #1 FLOW CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
45 | ZT-DO1043-A3 | ZT | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,2/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
91 | ZT-DO1043-B3 | ZT | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,3/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
137 | ZT-DO1043-C3 | ZT | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,4/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
183 | ZT-DO1043-D3 | ZT | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,5/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
107 | ZT-FA1005 | ZT | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
108 | ZT-FA1006 | ZT | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
109 | ZT-FA1007 | ZT | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
110 | ZT-FA1008 | ZT | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
111 | ZT-FA1009 | ZT | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
112 | ZT-FA1010 | ZT | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
113 | ZT-FA1011 | ZT | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
114 | ZT-FA1012 | ZT | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
115 | ZT-FA1013 | ZT | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
116 | ZT-FA1014 | ZT | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
117 | ZT-FA1015 | ZT | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
118 | ZT-FA1016 | ZT | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
119 | ZT-FA1017 | ZT | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
120 | ZT-FA1018 | ZT | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
121 | ZT-FA1019 | ZT | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
122 | ZT-FA1020 | ZT | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
123 | ZT-FA1021 | ZT | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
124 | ZT-FA1022 | ZT | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
125 | ZT-FA1023 | ZT | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
126 | ZT-FA1024 | ZT | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
127 | ZT-FA1025 | ZT | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
128 | ZT-FA1026 | ZT | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
46 | ZT-FA1043-A | ZT | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,2/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
92 | ZT-FA1043-B | ZT | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,3/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
138 | ZT-FA1043-C | ZT | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,4/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
184 | ZT-FA1043-D | ZT | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,5/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
19 | ZT-FA1053-1 | ZT | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-052 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
129 | ZT-FA1054-1 | ZT | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
59 | ZT-FA1055-A1 | ZT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE POSITION TRANSMITTER | PD-054 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
60 | ZT-FA1055-B1 | ZT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE POSITION TRANSMITTER | PD-054 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
34 | ZT-FG1056-1 | ZT | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE CONTROL DAMPER POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
81 | ZT-FG1116-A | ZT | FG1116-A | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-1 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
82 | ZT-FG1116-B | ZT | FG1116-B | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-2 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
83 | ZT-FG1116-C | ZT | FG1116-C | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-3 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
84 | ZT-FG1116-D | ZT | FG1116-D | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-4 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
85 | ZT-FG1117-A | ZT | FG1117-A | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-1 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
86 | ZT-FG1117-B | ZT | FG1117-B | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-2 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
87 | ZT-FG1117-C | ZT | FG1117-C | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-3 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
88 | ZT-FG1117-D | ZT | FG1117-D | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-4 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
50 | ZT-FW1001 | ZT | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
51 | ZT-FW1002 | ZT | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
52 | ZT-FW1060 | ZT | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
53 | ZT-FW1110-1 | ZT | FW1110-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
54 | ZT-FW1110-2 | ZT | FW1110-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
55 | ZT-FW1120-1 | ZT | FW1120-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
56 | ZT-FW1120-2 | ZT | FW1120-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
57 | ZT-FW1130-1 | ZT | FW1130-1 | #1 BOILER FEEDWATER FLOW CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
58 | ZT-FW1130-2 | ZT | FW1130-2 | #1 BOILER FEEDWATER FLOW CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
59 | ZT-FW1150 | ZT | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
60 | ZT-FW1391 | ZT | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
61 | ZT-FW1392 | ZT | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
62 | ZT-HD1101-1 | ZT | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
63 | ZT-HD1101-2 | ZT | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
64 | ZT-HD1102-1 | ZT | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
65 | ZT-HD1102-2 | ZT | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
66 | ZT-HD1103-1 | ZT | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
67 | ZT-HD1103-2 | ZT | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
68 | ZT-HD1105-1 | ZT | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
69 | ZT-HD1105-2 | ZT | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
70 | ZT-HD1106-1 | ZT | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
71 | ZT-HD1106-2 | ZT | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
6 | ZT-HR1010 | ZT | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE POSITION TRANSMITTER | PD-012 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
7 | ZT-HR1391 | ZT | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV POSITION TRANSMITTER | PD-012 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
79 | ZT-IW0391 | ZT | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV POSITION TRANSMITTER | PD-025 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
35 | ZT-LO1756 | ZT | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING SCOOP TUBE POSITION TRANSMITTER | PD-051 | - | - | 0~100% | WET 4~21mA | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
2 | ZT-MS1001 | ZT | MS1001 | #1 MAIN STEAM BLOW OFF VALVE POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
3 | ZT-MS1020 | ZT | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
4 | ZT-MS1391 | ZT | MS1391 | #1 MAIN STEAM SHUT-OFF MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
5 | ZT-MS1392 | ZT | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
48 | ZT-MU1001 | ZT | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
49 | ZT-MU1110 | ZT | MU1110 | #1 CONDENER MAKEUP WATER LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
34 | ZT-SB1001 | ZT | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV POSITION TRANSMITTER | PD-015 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
35 | ZT-SB1053 | ZT | SB1053 | #1 SOOT BLOWING STEAM PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-015 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
8 | ZT-TS1001 | ZT | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
9 | ZT-TS1002 | ZT | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
10 | ZT-TS1003 | ZT | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
11 | ZT-TS1004 | ZT | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
12 | ZT-TS1005 | ZT | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
13 | ZT-TS1389 | ZT | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
14 | ZT-TS1390 | ZT | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
15 | ZT-TS1391 | ZT | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
16 | ZT-TS1392 | ZT | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
17 | ZT-TS1393 | ZT | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
18 | ZT-TS1394 | ZT | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
19 | ZT-TS1395 | ZT | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
20 | ZT-TS1396 | ZT | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
21 | ZT-TS1397 | ZT | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
22 | ZT-TS1398 | ZT | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER(DEAERATORR SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
23 | ZT-TS1399 | ZT | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
24 | ZT-TS1400 | ZT | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZT

## MASTER
[6 empty] | DESIGN CONDITION |  |  |  | CONNECTION |  |  |  |  | R
E
ITEM | TAG. NO. |  |  |  | P&ID DWG NO. | P(Kg/c㎡G) | T( ℃ ) | RANGE | SIGNAL | FROM | TO | TYPE | SUPPLY SCOPE | REMARKS | V |  | TYPE/PACKAGE
52 | PT-IA1064-A | PT | IA1064-A | # 1 AIR BUFFER TANK OF BIASING DAMPER A PRESSURE TRANSMITTER | PD-023,6/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
53 | PT-IA1064-B | PT | IA1064-B | # 1 AIR BUFFER TANK OF BIASING DAMPER B PRESSURE TRANSMITTER | PD-023,6/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
5 | LS-CL1061-A4 | LS | CL1061-A4 | #1 A-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
6 | LS-CL1061-A5 | LS | CL1061-A5 | #1 A-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
7 | LS-CL1061-A6 | LS | CL1061-A6 | #1 A-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
1 | FT-CL1061-A | FT | CL1061-A | #1 A-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
17 | PS-IA1061-A1 | PS | IA1061-A1 | #1 A-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
19 | PS-IA1061-A2 | PS | IA1061-A2 | #1 A-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
46 | ZSC-CL1061-A1 | ZSC | CL1061-A1 | #1 A-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
55 | ZSO-CL1061-A1 | ZSO | CL1061-A1 | #1 A-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
47 | ZSC-CL1061-A2 | ZSC | CL1061-A2 | #1 A-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
56 | ZSO-CL1061-A2 | ZSO | CL1061-A2 | #1 A-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
37 | WT-CL1061-A1 | WT | CL1061-A1 | #1 A-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
38 | WT-CL1061-A2 | WT | CL1061-A2 | #1 A-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
4 | LS-CL1061-A3 | LS | CL1061-A3 | #1 A-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
43 | XV-CL1061-A7 | XV | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
48 | ZSC-CL1061-A7 | ZSC | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
57 | ZSO-CL1061-A7 | ZSO | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
31 | SV-CL1061-A7 | SV | CL1061-A7 | #1 A-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
28 | SE-CL1061-A | SE | CL1061-A | #1 A-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
34 | TS-CL1061-A | TS | CL1061-A | #1 A-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
91 | PG-IA1064-A | PG | IA1064-A | #1 AIR BUFFER TANK OF BIASING DAMPER A PRESSURE GAUGE | PD-023,5/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
92 | PG-IA1064-B | PG | IA1064-B | #1 AIR BUFFER TANK OF BIASING DAMPER B PRESSURE GAUGE | PD-023,5/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
90 | PG-IA1128 | PG | IA1128 | #1 AIR BUFFER TANK OF TURNING GEAR PRESSURE GAUGE | PD-023,4/6 | 10 | 60 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
50 | PT-IA1128 | PT | IA1128 | #1 AIR BUFFER TANK OF TURNING GEAR PRESSURE TRANSMITTER | PD-023,4/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
3 | PG-PA1052 | PG | PA1052 | #1 AIR PRE-HEATER AIR MOTOR SUPPLY PRESSURE GAUGE | - | - | - | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (AIR PRE HEATER) | NEW ADDED | 1 |  | AIR PREHEATER
17 | TE-FA1052-7 | TE | FA1052-7 | #1 AIR PRE-HEATER BOOTOM BEARING TEMPERATUTRE | - | - | - | -200~850℃ | AI | FIELD | TT | RTD | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
19 | TT-FA1052-7 | TT | FA1052-7 | #1 AIR PRE-HEATER BOOTOM BEARING TEMPERATUTRE TRANSMITTER | - | - | - | 0~150℃ | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
17 | DPT-FG1052-5 | DPT | FG1052-5 | #1 AIR PREHEATER DIFFERENTIAL PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~3300 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
11 | TE-FA1052-1 | TE | FA1052-1 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-1 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
12 | TE-FA1052-2 | TE | FA1052-2 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-2 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
13 | TE-FA1052-3 | TE | FA1052-3 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-3 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
14 | TE-FA1052-4 | TE | FA1052-4 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-4 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
15 | TE-FA1052-5 | TE | FA1052-5 | #1 AIR PRE-HEATER FIRE DETECTION THERMOCOUPLE-5 | - | - | - | 0-1100℃ | AI | FIELD | LCP | T/C | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
64 | PT-FG1121 | PT | FG1121 | #1 AIR PRE-HEATER GAS INLET PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 371 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
162 | TT-FG1124 | TT | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
163 | TT-FG1125 | TT | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 371 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
203 | TW-FG1124 | TW | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 371 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
199 | TE-FG1124 | TE | FG1124 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 371 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
204 | TW-FG1125 | TW | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(B) | PD-051 | ±890mmH2O | 371 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
200 | TE-FG1125 | TE | FG1125 | #1 AIR PRE-HEATER GAS INLET TEMPERATURE ELEMENT(B) | PD-051 | ±890mmH2O | 371 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
30 | AT-FG1131 | AT | FG1131 | #1 AIR PRE-HEATER GAS OUTLET FLUE GAS O2 (C) | PD-051 | ±890mmAq | 200 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0 |  | AT
65 | PT-FG1134 | PT | FG1134 | #1 AIR PRE-HEATER GAS OUTLET PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
164 | TT-FG1132 | TT | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
165 | TT-FG1133 | TT | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
205 | TW-FG1132 | TW | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
201 | TE-FG1132 | TE | FG1132 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
206 | TW-FG1133 | TW | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
202 | TE-FG1133 | TE | FG1133 | #1 AIR PRE-HEATER GAS OUTLET TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
1 | LG-FA1052-1 | LG | FA1052-1 | #1 AIR PRE-HEATER LEVEL GLASS BOTTOM BERATING | - | - | - | - | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
2 | LG-FA1052-2 | LG | FA1052-2 | #1 AIR PRE-HEATER LEVEL GLASS TOP BERATING | - | - | - | - | - | - |  | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
8 | ST-FA1502-1 | ST | FA1502-1 | #1 AIR PRE-HEATER ROTOR SPEED MONITOR-1 | - | - | - | 0-20000 | AI | LCP | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
9 | ST-FA1502-2 | ST | FA1502-2 | #1 AIR PRE-HEATER ROTOR SPEED MONITOR-2 | - | - | - | 0-20000 | AI | LCP | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
6 | SE-FA1052-1 | SE | FA1052-1 | #1 AIR PRE-HEATER ROTOR SPEED SENSOR-1 | - | - | - | 0-12 mm | AI | FIELD | SM-1 | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
7 | SE-FA1052-2 | SE | FA1052-2 | #1 AIR PRE-HEATER ROTOR SPEED SENSOR-2 | - | - | - | 0-12 mm | AI | FIELD | SM-2 | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
10 | SV-FA1052-1 | SV | FA1052-1 | #1 AIR PRE-HEATER SOLENOID FOR AIR MOTOR | - | - | 0-10 BarG | - | DO | DCS | LOCAL INVERTER PANEL | 24VDC | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
16 | TE-FA1052-6 | TE | FA1052-6 | #1 AIR PRE-HEATER TOP BEARING TEMPERATUTRE | - | - | - | -200~850℃ | AI | FIELD | TT | RTD | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
18 | TT-FA1052-6 | TT | FA1052-6 | #1 AIR PRE-HEATER TOP BEARING TEMPERATUTRE TRANSMITTER | - | - | - | 0~150℃ | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
141 | TE-CW1108-A3 | TE | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR BEARING TEMPERATURE-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
142 | TE-CW1108-A4 | TE | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR BEARING TEMPERATURE-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
103 | TT-CW1108-A3 | TT | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
31 | VT-CW1108-A3 | VT | CW1108-A3 | #1 AUXILIARY COOLING PUMP (A) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
104 | TT-CW1108-A4 | TT | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR REAR BEARING TEMPERATURE TRANSMITTER-2 | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
32 | VT-CW1108-A4 | VT | CW1108-A4 | #1 AUXILIARY COOLING PUMP (A) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
143 | TE-CW1108-AU1 | TE | CW1108-AU1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
144 | TE-CW1108-AU2 | TE | CW1108-AU2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
105 | TT-CW1108-AU | TT | CW1108-AU | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
145 | TE-CW1108-AV1 | TE | CW1108-AV1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
146 | TE-CW1108-AV2 | TE | CW1108-AV2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
106 | TT-CW1108-AV | TT | CW1108-AV | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
147 | TE-CW1108-AW1 | TE | CW1108-AW1 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
148 | TE-CW1108-AW2 | TE | CW1108-AW2 | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
107 | TT-CW1108-AW | TT | CW1108-AW | #1 AUXILIARY COOLING PUMP (A) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
149 | TE-CW1108-B3 | TE | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR BEARING TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
150 | TE-CW1108-B4 | TE | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR BEARING TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
108 | TT-CW1108-B3 | TT | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
33 | VT-CW1108-B3 | VT | CW1108-B3 | #1 AUXILIARY COOLING PUMP (B) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
109 | TT-CW1108-B4 | TT | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
34 | VT-CW1108-B4 | VT | CW1108-B4 | #1 AUXILIARY COOLING PUMP (B) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-021 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (AUXILIARY COOLING PUMP) | RESERVED 20150408 | 0 |  | VT
151 | TE-CW1108-BU1 | TE | CW1108-BU1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
152 | TE-CW1108-BU2 | TE | CW1108-BU2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
110 | TT-CW1108-BU | TT | CW1108-BU | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
153 | TE-CW1108-BV1 | TE | CW1108-BV1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
154 | TE-CW1108-BV2 | TE | CW1108-BV2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
111 | TT-CW1108-BV | TT | CW1108-BV | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
155 | TE-CW1108-BW1 | TE | CW1108-BW1 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
156 | TE-CW1108-BW2 | TE | CW1108-BW2 | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (AUXILIARY COOLING PUMP) |  | 0 |  | TE
112 | TT-CW1108-BW | TT | CW1108-BW | #1 AUXILIARY COOLING PUMP (B) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-021 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
139 | TW-CW1151 | TW | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
64 | TG-CW1151 | TG | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
13 | LG-CW1109 | LG | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL GAUGE | PD-021 | 10 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
25 | LSLL-CW1109 | LSLL | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL LOW-LOW SWITCH | PD-021 | 10 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0 |  | LS
19 | LT-CW1109 | LT | CW1109 | #1 AUXILIARY COOLING WATER EXPANSION TANK LEVEL TRANSMITTER | PD-021 | 10 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
81 | PG-CW1151 | PG | CW1151 | #1 AUXILIARY COOLING WATER EXPANSION TANK OUTLET PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
55 | PG-SW1107-A1 | PG | SW1107-A1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
56 | PG-SW1107-A2 | PG | SW1107-A2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
118 | TW-SW1107-A | TW | SW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
134 | TW-CW1107-A | TW | CW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
47 | TG-SW1107-A | TG | SW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
59 | TG-CW1107-A | TG | CW1107-A | #1 AUXILIARY COOLING WATER HEAT EXCHANGER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
57 | PG-SW1107-B1 | PG | SW1107-B1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
58 | PG-SW1107-B2 | PG | SW1107-B2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
119 | TW-SW1107-B | TW | SW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
135 | TW-CW1107-B | TW | CW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
48 | TG-SW1107-B | TG | SW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
60 | TG-CW1107-B | TG | CW1107-B | #1 AUXILIARY COOLING WATER HEAT EXCHANGER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
59 | PG-SW1107-C1 | PG | SW1107-C1 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
60 | PG-SW1107-C2 | PG | SW1107-C2 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
120 | TW-SW1107-C | TW | SW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
136 | TW-CW1107-C | TW | CW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
49 | TG-SW1107-C | TG | SW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
61 | TG-CW1107-C | TG | CW1107-C | #1 AUXILIARY COOLING WATER HEAT EXCHANGER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
78 | PG-SW1552 | PG | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
133 | TW-SW1552 | TW | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
58 | TG-SW1552 | TG | SW1552 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER INLET TEMPERATURE GAUGE | PD-020 | 7 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
36 | PT-CW1153 | PT | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
142 | TW-CW1153 | TW | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
158 | TE-CW1153 | TE | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
114 | TT-CW1153 | TT | CW1153 | #1 AUXILIARY COOLING WATER HEAT EXCHANGER OUTLET COMMON HEADER TEMPERATURE TRANSMITTER | PD-021 | 10 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
27 | PT-CW1156 | PT | CW1156 | #1 AUXILIARY COOLING WATER PRESSURE TRANSMITTER AT BOTTOM ASH SCREW CONVEYOR COMMON HEADER | PD-072 | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
82 | PG-CW1157-A | PG | CW1157-A | #1 AUXILIARY COOLING WATER PUMP (A) SUCTION PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
83 | PG-CW1157-B | PG | CW1157-B | #1 AUXILIARY COOLING WATER PUMP (B) SUCTION PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
79 | PG-CW1108-A | PG | CW1108-A | #1 AUXILIARY COOLING WATER PUMP A DISCHARGE PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
9 | DPT-CW1108-A | DPT | CW1108-A | #1 AUXILIARY COOLING WATER PUMP A STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
80 | PG-CW1108-B | PG | CW1108-B | #1 AUXILIARY COOLING WATER PUMP B DISCHARGE PRESSURE GAUGE | PD-021 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
10 | DPT-CW1108-B | DPT | CW1108-B | #1 AUXILIARY COOLING WATER PUMP B STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
35 | PT-CW1152 | PT | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE PRESSURE TRANSMITTER | PD-021 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
140 | TW-CW1152 | TW | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
157 | TE-CW1152 | TE | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE ELEMENT | PD-021 | 10 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
141 | TW-CW1152 | TW | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
65 | TG-CW1152 | TG | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
113 | TT-CW1152 | TT | CW1152 | #1 AUXILIARY COOLING WATER PUMP COMMON DISCHARGE TEMPERATURE TRANSMITTER | PD-021 | 10 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
2 | TT-CW1156 | TT | CW1156 | #1 AUXILIARY COOLING WATER TEMPERATURE AT BOTTOM ASH SCREW CONVEYOR COMMON HEADER | PD-021 | - | - | 0~150℃ | AI 4~20mA | FIELD | DCS | SMART | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
1 | TE-CW1156 | TE | CW1156 | #1 AUXILIARY COOLING WATER TEMPERATURE ELEMENT AT ASH CONVEYOR COMMON HEADER | PD-021 | - | - | - | - | FIELD | TT | RTD | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
23 | MV-AS1392 | MV | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
87 | ZSC-AS1392 | ZSC | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
88 | ZSO-AS1392 | ZSO | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
30 | ZT-AS1392 | ZT | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
89 | TS-AS1392 | TS | AS1392 | #1 AUXILIARY STEAM HEADER DRAIN MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
15 | PT-AS1004 | PT | AS1004 | #1 AUXILIARY STEAM HEADER PRESSURE TRANSMITTER | PD-014 | 13 | 390 | 0~15 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
16 | PT-AS1005 | PT | AS1005 | #1 AUXILIARY STEAM HEADER PRESSURE TRANSMITTER | PD-014 | 13 | 390 | 0~15 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
50 | TW-AS1003 | TW | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
31 | TE-AS1003 | TE | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
20 | TT-AS1003 | TT | AS1003 | #1 AUXILIARY STEAM HEADER TEMPERATURE TRANSMITTER | PD-014 | 13 | 390 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
66 | PG-SW1113-2 | PG | SW1113-2 | #1 BALL RECIRCULATING PUMP M-1113 DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~4 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
65 | PG-SW1113-1 | PG | SW1113-1 | #1 BALL RECIRCULATING PUMP M-1113 SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~2.5 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
68 | PG-SW1114-2 | PG | SW1114-2 | #1 BALL RECIRCULATING PUMP M-1114 DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~4 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
67 | PG-SW1114-1 | PG | SW1114-1 | #1 BALL RECIRCULATING PUMP M-1114 SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~2.5 | - | - | - | BOURDON | PACKAGE (TUBE CLEANING) |  | 0 |  | PG
5 | DPT-SW1111 | DPT | SW1111 | #1 BALL SEPARATOR L-1111 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~100mBar | AI 4~20mA | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | DPT
6 | DPT-SW1112 | DPT | SW1112 | #1 BALL SEPARATOR L-1112 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~100mBar | AI 4~20mA | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | DPT
45 | MV-SW1005 | MV | SW1005 | #1 BALL VESSEL T-1115 INLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
195 | ZSC-SW1005 | ZSC | SW1005 | #1 BALL VESSEL T-1115 INLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
196 | ZSO-SW1005 | ZSO | SW1005 | #1 BALL VESSEL T-1115 INLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
197 | TS-SW1005 | TS | SW1005 | #1 BALL VESSEL T-1115 INLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
46 | MV-SW1006 | MV | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
198 | ZSC-SW1006 | ZSC | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
199 | ZSO-SW1006 | ZSO | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
200 | TS-SW1006 | TS | SW1006 | #1 BALL VESSEL T-1115 OUTLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
43 | MV-SW1003 | MV | SW1003 | #1 BALL VESSEL T-1116 INLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
189 | ZSC-SW1003 | ZSC | SW1003 | #1 BALL VESSEL T-1116 INLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
190 | ZSO-SW1003 | ZSO | SW1003 | #1 BALL VESSEL T-1116 INLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
191 | TS-SW1003 | TS | SW1003 | #1 BALL VESSEL T-1116 INLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
44 | MV-SW1004 | MV | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (TUBE CLEANING) |  | 0 |  | MV
192 | ZSC-SW1004 | ZSC | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
193 | ZSO-SW1004 | ZSO | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
194 | TS-SW1004 | TS | SW1004 | #1 BALL VESSEL T-1116 OUTLET MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (TUBE CLEANING) | NEW ADDED | 0 |  | ZS
9 | LS-CL1061-B4 | LS | CL1061-B4 | #1 B-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
10 | LS-CL1061-B5 | LS | CL1061-B5 | #1 B-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
11 | LS-CL1061-B6 | LS | CL1061-B6 | #1 B-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
2 | FT-CL1061-B | FT | CL1061-B | #1 B-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
21 | PS-IA1061-B1 | PS | IA1061-B1 | #1 B-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
23 | PS-IA1061-B2 | PS | IA1061-B2 | #1 B-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
49 | ZSC-CL1061-B1 | ZSC | CL1061-B1 | #1 B-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
58 | ZSO-CL1061-B1 | ZSO | CL1061-B1 | #1 B-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
50 | ZSC-CL1061-B2 | ZSC | CL1061-B2 | #1 B-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
59 | ZSO-CL1061-B2 | ZSO | CL1061-B2 | #1 B-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
39 | WT-CL1061-B1 | WT | CL1061-B1 | #1 B-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
40 | WT-CL1061-B2 | WT | CL1061-B2 | #1 B-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
8 | LS-CL1061-B3 | LS | CL1061-B3 | #1 B-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
44 | XV-CL1061-B7 | XV | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
51 | ZSC-CL1061-B7 | ZSC | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
60 | ZSO-CL1061-B7 | ZSO | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
32 | SV-CL1061-B7 | SV | CL1061-B7 | #1 B-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
29 | SE-CL1061-B | SE | CL1061-B | #1 B-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
35 | TS-CL1061-B | TS | CL1061-B | #1 B-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
1 | DPG-FW1115-A | DPG | FW1115-A | #1 BFP(A) SUCTION STRAINER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~0.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
2 | DPG-FW1115-B | DPG | FW1115-B | #1 BFP(B) SUCTION STRAINER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~0.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
3 | DPT-FW1115-A | DPT | FW1115-A | #1 BFP(A) SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-017 | - | - | 0~0.6 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | PACKAGE (BFP) |  | 0 |  | DPT
4 | DPT-FW1115-B | DPT | FW1115-B | #1 BFP(B) SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-017 | - | - | 0~0.6 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | PACKAGE (BFP) |  | 0 |  | DPT
17 | FCV-FW1130-1 | FCV | FW1130-1 | #1 BOILER FEEDWATER FLOW CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
18 | FCV-FW1130-2 | FCV | FW1130-2 | #1 BOILER FEEDWATER FLOW CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
6 | FE-FW1007 | FE | FW1007 | #1 BOILER FEEDWATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~550 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
137 | TW-CW1115-A1 | TW | CW1115-A1 | #1 BFP MOTOR P-1115A COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
62 | TG-CW1115-A1 | TG | CW1115-A1 | #1 BFP MOTOR P-1115A COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
138 | TW-CW1115-B1 | TW | CW1115-B1 | #1 BFP MOTOR P-1115B COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
63 | TG-CW1115-B1 | TG | CW1115-B1 | #1 BFP MOTOR P-1115B COOLER OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
7 | FE-FW1059 | FE | FW1059 | #1 TURBINE BYPASS DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 100 | 180 | 0~40 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
8 | FE-FW1109 | FE | FW1109 | #1 SUPERHEATER PANEL #1 DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~40 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
9 | FE-FW1119 | FE | FW1119 | #1 SUPERHEATER PANEL #2 DESUPERHEATING SPRAY WATER FLOW ELEMENT | PD-017 | 230 | 275 | 0~40 | <5000 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
10 | FE-FW1149 | FE | FW1149 | #1 REHEATER INLET DESUPEREHEATEREATING SPRAY WATER FLOW ELEMENT | PD-017 | 100 | 180 | 0~25 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
36 | TG-LO1115-A1 | TG | LO1115-A1 | #1 BFP(A) LUBE OIL COOLER INLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | TG
37 | TG-LO1115-A2 | TG | LO1115-A2 | #1 BFP(A) LUBE OIL COOLER OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | TG
3 | DPG-LO1115-A | DPG | LO1115-A | #1 BFP(A) LUBE OIL INLET FILTER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~1.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
3 | LG-LO1115-A | LG | LO1115-A | #1 BFP(A) LUBE OIL LEVEL GAUGE | PD-017 | - | - | 380 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | LG
8 | LS-LO1115-A | LS | LO1115-A | #1 BFP(A) LUBE OIL LEVEL SWITCH (LOW ALARM) | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
40 | PG-LO1115-A1 | PG | LO1115-A1 | #1 BFP(A) LUBE OIL PRESSURE GAUGE-1 | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
41 | PG-LO1115-A2 | PG | LO1115-A2 | #1 BFP(A) LUBE OIL PRESSURE GAUGE-2 | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
5 | PS-LO1115-A1 | PS | LO1115-A1 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-1 (LOW ALARM/STANDBY PUMP START) | PD-017 | - | - | 1.5 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
6 | PS-LO1115-A2 | PS | LO1115-A2 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-2 (NORMAL/START PERMISIVE FOR BFP) | PD-017 | - | - | 2.0 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
7 | PS-LO1115-A3 | PS | LO1115-A3 | #1 BFP(A) LUBE OIL PRESSURE SWITCH-3 (LOW-LOW/MAIN EQUIPMENT TRIP) | PD-017 | - | - | 1 | DI | FIELD | ARP | - | PACKAGE (BFP) |  | 0 |  | PS
38 | TG-LO1115-A3 | TG | LO1115-A3 | #1 BFP(A) LUBE OIL TANK TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | TG
6 | FT-FW1007-1 | FT | FW1007-1 | #1 BOILER FEEDWATER FLOW TRANSMITTER-1 | PD-017 | 230 | 275 | 0~550 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
7 | FT-FW1007-2 | FT | FW1007-2 | #1 BOILER FEEDWATER FLOW TRANSMITTER-2 | PD-017 | 230 | 275 | 0~550 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
8 | FT-FW1059 | FT | FW1059 | #1 TURBINE BYPASS DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 100 | 180 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
9 | FT-FW1109 | FT | FW1109 | #1 SUPERHEATER PANEL #1 DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 230 | 275 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
10 | FT-FW1119 | FT | FW1119 | #1 SUPERHEATER PANEL #2 DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 230 | 275 | 0~40 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
11 | FT-FW1149 | FT | FW1149 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER FLOW TRANSMITTER | PD-017 | 100 | 180 | 0~25 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
6 | LS-FW1115-A | LS | FW1115-A | #1 BFP(A) MOTOR LEAKAGE DETECTOR | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
7 | LS-FW1115-B | LS | FW1115-B | #1 BFP(B) MOTOR LEAKAGE DETECTOR | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
34 | MV-FW1001 | MV | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
35 | MV-FW1002 | MV | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
36 | MV-FW1391 | MV | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
37 | MV-FW1392 | MV | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV | PD-017 | 230 | 180 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
24 | PG-FW1105-1 | PG | FW1105-1 | #1 HIGH PRESSURE HEATER NO.1 INLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 180 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
25 | PG-FW1105-2 | PG | FW1105-2 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 220 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
26 | PG-FW1106-1 | PG | FW1106-1 | #1 HIGH PRESSURE HEATER NO.2 INLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 220 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
27 | PG-FW1106-2 | PG | FW1106-2 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER PRESSURE GAUGE | PD-017 | 230 | 275 | 0~250 | - | - | - | BOURDON | FHI |  | 0 |  | PG
28 | PG-FW1115-A1 | PG | FW1115-A1 | #1 BFP(A) DISCHAEGE PRESSURE GAUGE | PD-017 | - | - | 0~250 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
29 | PG-FW1115-A2 | PG | FW1115-A2 | #1 BFP(A) BLEED OFF PRESSURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
30 | PG-FW1115-A3 | PG | FW1115-A3 | #1 BFP(A) SUCTION PRESSURE GAUGE | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
31 | PG-FW1115-A4 | PG | FW1115-A4 | #1 BFP(A) BALANCE LINE PRESSURE GAUGE | PD-017 | - | - | 0~25 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
32 | PG-FW1115-A5 | PG | FW1115-A5 | #1 BFP(A) PUMP DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
33 | PG-FW1115-A6 | PG | FW1115-A6 | #1 BFP(A) PUMP NON DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
34 | PG-FW1115-B1 | PG | FW1115-B1 | #1 BFP(B) DISCHAEGE PRESSURE GAUGE | PD-017 | - | - | 0~250 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
35 | PG-FW1115-B2 | PG | FW1115-B2 | #1 BFP(B) BLEED OFF PRESSURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
36 | PG-FW1115-B3 | PG | FW1115-B3 | #1 BFP(B) SUCTION PRESSURE GAUGE | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
37 | PG-FW1115-B4 | PG | FW1115-B4 | #1 BFP(B) BALANCE LINE PRESSURE GAUGE | PD-017 | - | - | 0~25 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
38 | PG-FW1115-B5 | PG | FW1115-B5 | #1 BFP(B) PUMP DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
39 | PG-FW1115-B6 | PG | FW1115-B6 | #1 BFP(B) PUMP NON DRIVEN END BEARING LUBE OIL INLET PRESSURE GAUGE | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
22 | PT-FW1011 | PT | FW1011 | #1 BFP COMMON DISCHARGE WATER PRESSURE TRANSMITTER | PD-017 | 230 | 180 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
23 | PT-FW1115-A | PT | FW1115-A | #1 BFP(A) SUCTION PRESSURE TRANSMITTER | PD-017 | 10 | 180 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
24 | PT-FW1115-B | PT | FW1115-B | #1 BFP(B) SUCTION PRESSURE TRANSMITTER | PD-017 | 10 | 180 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
30 | PT-FW1160 | PT | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER PRESSURE TRANSMITTER | PD-019 | 230 | 275 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
20 | SV-FW1060 | SV | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE SOLENOID VALVE(QUICK OPEN) | PD-017 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
21 | SV-FW1061 | SV | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
22 | SV-FW1111-1 | SV | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
23 | SV-FW1111-2 | SV | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
24 | SV-FW1121-1 | SV | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
25 | SV-FW1121-2 | SV | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
26 | SV-FW1151 | SV | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-017 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
19 | TCV-FW1060 | TCV | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 100 | 180 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
20 | TCV-FW1110-1 | TCV | FW1110-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
21 | TCV-FW1110-2 | TCV | FW1110-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
22 | TCV-FW1120-1 | TCV | FW1120-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
23 | TCV-FW1120-2 | TCV | FW1120-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP | PD-017 | 230 | 275 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
24 | TCV-FW1150 | TCV | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-017 | 100 | 180 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
66 | TE-FW1010 | TE | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 10 | 180 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
67 | TE-FW1011 | TE | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE ELEMENT | PD-017 | 230 | 180 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
68 | TE-FW1105 | TE | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 220 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
69 | TE-FW1106 | TE | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 275 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
70 | TE-FW1115-A1 | TE | FW1115-A1 | #1 BFP(A) PUMP SIDE BEARING FRONT(NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
71 | TE-FW1115-A2 | TE | FW1115-A2 | #1 BFP(A) PUMP BEARING REAR(DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
72 | TE-FW1115-A3 | TE | FW1115-A3 | #1 BFP(A) MOTOR SIDE BEARING REAR (DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
73 | TE-FW1115-A4 | TE | FW1115-A4 | #1 BFP(A) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
74 | TE-FW1115-AU1 | TE | FW1115-AU1 | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
39 | TG-LO1115-B1 | TG | LO1115-B1 | #1 BFP(B) LUBE OIL COOLER INLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0 |  | TG
40 | TG-LO1115-B2 | TG | LO1115-B2 | #1 BFP(B) LUBE OIL COOLER OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0 |  | TG
4 | DPG-LO1115-B | DPG | LO1115-B | #1 BFP(B) LUBE OIL INLET FILTER DIFFERENTIAL PRESSURE GAUGE | PD-017 | - | - | 0~1.6 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | DPG
4 | LG-LO1115-B | LG | LO1115-B | #1 BFP(B) LUBE OIL LEVEL GAUGE | PD-017 | - | - | 380 | - | - | - | - | PACKAGE (BFP) |  | 0 |  | LG
9 | LS-LO1115-B | LS | LO1115-B | #1 BFP(B) LUBE OIL LEVEL SWITCH (LOW ALARM) | PD-017 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | LS
42 | PG-LO1115-B1 | PG | LO1115-B1 | #1 BFP(B) LUBE OIL PRESSURE GAUGE-1 | PD-017 | - | - | 0~10 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
43 | PG-LO1115-B2 | PG | LO1115-B2 | #1 BFP(B) LUBE OIL PRESSURE GAUGE-2 | PD-017 | - | - | 0~6 | - | - | - | BOURDON | PACKAGE (BFP) |  | 0 |  | PG
8 | PS-LO1115-B1 | PS | LO1115-B1 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-1 (LOW ALARM/STANDBY PUMP START) | PD-017 | - | - | 1.5 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
9 | PS-LO1115-B2 | PS | LO1115-B2 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-2 (NORMAL/START PERMISIVE FOR BFP) | PD-017 | - | - | 2.0 | DI | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | PS
10 | PS-LO1115-B3 | PS | LO1115-B3 | #1 BFP(B) LUBE OIL PRESSURE SWITCH-3 (LOW-LOW/MAIN EQUIPMENT TRIP) | PD-017 | - | - | 1 | DI | FIELD | ARP | - | PACKAGE (BFP) |  | 0 |  | PS
41 | TG-LO1115-B3 | TG | LO1115-B3 | #1 BFP(B) LUBE OIL TANK TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-MENTAL | PACKAGE (BFP) |  | 0 |  | TG
75 | TE-FW1115-AU2 | TE | FW1115-AU2 | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
76 | TE-FW1115-AV1 | TE | FW1115-AV1 | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
77 | TE-FW1115-AV2 | TE | FW1115-AV2 | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
78 | TE-FW1115-AW1 | TE | FW1115-AW1 | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
79 | TE-FW1115-AW2 | TE | FW1115-AW2 | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
80 | TE-FW1115-B1 | TE | FW1115-B1 | #1 BFP(B) PUMP BEARING FRONT(NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
81 | TE-FW1115-B2 | TE | FW1115-B2 | #1 BFP(B) PUMP BEARING REAR(DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) |  | 0 |  | TE
82 | TE-FW1115-B3 | TE | FW1115-B3 | #1 BFP(B) MOTOR SIDE BEARING REAR (DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
83 | TE-FW1115-B4 | TE | FW1115-B4 | #1 BFP(B) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE ELEMENT | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
84 | TE-FW1115-BU-1 | TE | FW1115-BU-1 | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
85 | TE-FW1115-BU-2 | TE | FW1115-BU-2 | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-017 |  |  | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
86 | TE-FW1115-BV-1 | TE | FW1115-BV-1 | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
87 | TE-FW1115-BV-2 | TE | FW1115-BV-2 | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-017 |  |  | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
88 | TE-FW1115-BW-1 | TE | FW1115-BW-1 | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE ELEMENT-1 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
89 | TE-FW1115-BW-2 | TE | FW1115-BW-2 | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE ELEMENT-2 | PD-017 | - | - | - | - | FIELD | TT | RTD | PACKAGE (BFP) | NEW ADDED | 0 |  | TE
106 | TE-FW1160 | TE | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 230 | 275 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
20 | TG-FW1115-A1 | TG | FW1115-A1 | #1 BFP(A) PUMP DISCHARGE TEMPERATURE GAUGE | PD-017 | - | - | 0~300 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
21 | TG-FW1115-A2 | TG | FW1115-A2 | #1 BFP(A) PLAN 23 FLUSHING IN LINE DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
22 | TG-FW1115-A3 | TG | FW1115-A3 | #1 BFP(A) PLAN 23 FLUSHING IN LINE NON DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
23 | TG-FW1115-A4 | TG | FW1115-A4 | #1 BFP(A) PUMP DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
24 | TG-FW1115-A5 | TG | FW1115-A5 | #1 BFP(A) PUMP NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
25 | TG-FW1115-A6 | TG | FW1115-A6 | #1 BFP(A) MOTOR DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
26 | TG-FW1115-A7 | TG | FW1115-A7 | #1 BFP(A) MOTOR NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
27 | TG-FW1115-A8 | TG | FW1115-A8 | #1 BFP(A) COOLING WATER OUTLET HEADER TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
28 | TG-FW1115-B1 | TG | FW1115-B1 | #1 BFP(B) PUMP DISCHARGE TEMPERATURE GAUGE | PD-017 | - | - | 0~300 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
29 | TG-FW1115-B2 | TG | FW1115-B2 | #1 BFP(B) PLAN 23 FLUSHING IN LINE DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
30 | TG-FW1115-B3 | TG | FW1115-B3 | #1 BFP(B) PLAN 23 FLUSHING IN LINE NON DRIVEN END TEMPERATURE GAUGE | PD-017 | - | - | 0~200 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
31 | TG-FW1115-B4 | TG | FW1115-B4 | #1 BFP(B) PUMP DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
32 | TG-FW1115-B5 | TG | FW1115-B5 | #1 BFP(B) PUMP NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
33 | TG-FW1115-B6 | TG | FW1115-B6 | #1 BFP(B) MOTOR DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
34 | TG-FW1115-B7 | TG | FW1115-B7 | #1 BFP(B) MOTOR NON DRIVEN END BEARING LUBE OIL OUTLET TEMPERATURE GAUGE | PD-017 | - | - | 0~120 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
35 | TG-FW1115-B8 | TG | FW1115-B8 | #1 BFP(B) COOLING WATER OUTLET HEADER TEMPERATURE GAUGE | PD-017 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (BFP) |  | 0 |  | TG
46 | TG-FW1160 | TG | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE GAUGE | PD-019 | 230 | 275 | 0~400 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
146 | TS-FW1001 | TS | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
149 | TS-FW1002 | TS | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
170 | TS-FW1391 | TS | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
173 | TS-FW1392 | TS | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
49 | TT-FW1010 | TT | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 10 | 180 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
50 | TT-FW1011 | TT | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 180 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
51 | TT-FW1105 | TT | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 220 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
52 | TT-FW1106 | TT | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-017 | 230 | 275 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
53 | TT-FW1115-A1 | TT | FW1115-A1 | #1 BFP(A) PUMP SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
54 | TT-FW1115-A2 | TT | FW1115-A2 | #1 BFP(A) PUMP SIDE BEARING FRONT(DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
55 | TT-FW1115-A3 | TT | FW1115-A3 | #1 BFP(A) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
56 | TT-FW1115-A4 | TT | FW1115-A4 | #1 BFP(A) MOTOR SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
57 | TT-FW1115-AU | TT | FW1115-AU | #1 BFP(A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
58 | TT-FW1115-AV | TT | FW1115-AV | #1 BFP(A) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
59 | TT-FW1115-AW | TT | FW1115-AW | #1 BFP(A) MOTOR WINDING (W)TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
60 | TT-FW1115-B1 | TT | FW1115-B1 | #1 BFP(B) PUMP SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
61 | TT-FW1115-B2 | TT | FW1115-B2 | #1 BFP(B) PUMP SIDE BEARING FRONT(DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
39 | MV-BD1002 | MV | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV | PD-019 | 155.4 | 343 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
177 | ZSC-BD1002 | ZSC | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
178 | ZSO-BD1002 | ZSO | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
73 | ZT-BD1002 | ZT | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
179 | TS-BD1002 | TS | BD1002 | #1 BOILER CONTINUOUS BLOWDOWN MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
62 | TT-FW1115-B3 | TT | FW1115-B3 | #1 BFP(B) MOTOR SIDE BEARING FRONT (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
63 | TT-FW1115-B4 | TT | FW1115-B4 | #1 BFP(B) MOTOR SIDE BEARING REAR (NON DRIVEN) END TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
64 | TT-FW1115-BU | TT | FW1115-BU | #1 BFP(B) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
65 | TT-FW1115-BV | TT | FW1115-BV | #1 BFP(B) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
66 | TT-FW1115-BW | TT | FW1115-BW | #1 BFP(B) MOTOR WINDING (W)TEMPERATURE TRANSMITTER | PD-017 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
83 | TT-FW1160 | TT | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 230 | 275 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
82 | TW-FW1010 | TW | FW1010 | #1 BFP INLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 10 | 180 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
1 | FE-MS1031 | FE | MS1031 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER FLOW ELEMENT | PD-011 | 144 | 550 | 0~500 | <5000 | - |  | FLOW NOZZLE | FHI |  | 0 |  | FE
1 | FT-MS1031 | FT | MS1031 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER FLOW TRANSMITTER | PD-011 | 144 | 550 | 0~500 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
1 | PG-MS1003 | PG | MS1003 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER PRESSURE GAUGE | PD-011 | 144 | 550 | 0~200 | - | - | - | BOURDON | FHI |  | 0 |  | PG
1 | PT-MS1002 | PT | MS1002 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER PRESSURE TRANSMITTER | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
4 | TW-MS1004-1 | TW | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
11 | TE-MS1004-1 | TE | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-1 | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
5 | TW-MS1004-2 | TW | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
12 | TE-MS1004-2 | TE | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE ELEMENT-2 | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
6 | TW-MS1005 | TW | MS1005 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE GAUGE | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
1 | TG-MS1005 | TG | MS1005 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE GAUGE | PD-011 | 144 | 550 | 0~700 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
1 | TT-MS1004-1 | TT | MS1004-1 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE TRANSMITTER-1 | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
2 | TT-MS1004-2 | TT | MS1004-2 | #1 BOILER FINISHING SUPERHEATER OUTLET HEADER TEMPERATURE TRANSMITTER-2 | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
38 | MV-BD1001 | MV | BD1001 | #1 BOILER MASS BLOWDOWN MOV | PD-019 | 155.4 | 343 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
174 | ZSC-BD1001 | ZSC | BD1001 | #1 BOILER MASS BLOWDOWN MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
175 | ZSO-BD1001 | ZSO | BD1001 | #1 BOILER MASS BLOWDOWN MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
72 | ZT-BD1001 | ZT | BD1001 | #1 BOILER MASS BLOWDOWN MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
176 | TS-BD1001 | TS | BD1001 | #1 BOILER MASS BLOWDOWN MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
3 | FS-CW1060-A1 | FS | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
4 | FS-CW1060-A2 | FS | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
68 | TT-CW1060-A1 | TT | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
69 | TT-CW1060-A2 | TT | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
11 | PG-CW1060-A | PG | CW1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
12 | PG-CW1060-A1 | PG | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
13 | PG-CW1060-A2 | PG | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
48 | TG-CW1060-A | TG | CW1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
49 | TG-CW1060-A1 | TG | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
50 | TG-CW1060-A2 | TG | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
40 | TE-CW1060-A1 | TE | CW1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
41 | TE-CW1060-A2 | TE | CW1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
60 | TT-BH1060-A1 | TT | BH1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
32 | TE-BH1060-A1 | TE | BH1060-A1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
61 | TT-BH1060-A2 | TT | BH1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
33 | TE-BH1060-A2 | TE | BH1060-A2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060A OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
23 | PG-PA1060-A | PG | PA1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
28 | SS-BH1060-A | SS | BH1060-A | #1 BOTTOM ASH SCREW CONVEYOR L-1060A SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
5 | FS-CW1060-B1 | FS | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
6 | FS-CW1060-B2 | FS | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
70 | TT-CW1060-B1 | TT | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
71 | TT-CW1060-B2 | TT | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
14 | PG-CW1060-B | PG | CW1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
15 | PG-CW1060-B1 | PG | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
16 | PG-CW1060-B2 | PG | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
51 | TG-CW1060-B | TG | CW1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
52 | TG-CW1060-B1 | TG | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
53 | TG-CW1060-B2 | TG | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
42 | TE-CW1060-B1 | TE | CW1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
43 | TE-CW1060-B2 | TE | CW1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
62 | TT-BH1060-B1 | TT | BH1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
34 | TE-BH1060-B1 | TE | BH1060-B1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
63 | TT-BH1060-B2 | TT | BH1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
35 | TE-BH1060-B2 | TE | BH1060-B2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060B OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
24 | PG-PA1060-B | PG | PA1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
29 | SS-BH1060-B | SS | BH1060-B | #1 BOTTOM ASH SCREW CONVEYOR L-1060B SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
7 | FS-CW1060-C1 | FS | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
8 | FS-CW1060-C2 | FS | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
72 | TT-CW1060-C1 | TT | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
73 | TT-CW1060-C2 | TT | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
17 | PG-CW1060-C | PG | CW1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
18 | PG-CW1060-C1 | PG | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
19 | PG-CW1060-C2 | PG | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
54 | TG-CW1060-C | TG | CW1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
55 | TG-CW1060-C1 | TG | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
56 | TG-CW1060-C2 | TG | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
44 | TE-CW1060-C1 | TE | CW1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
45 | TE-CW1060-C2 | TE | CW1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
64 | TT-BH1060-C1 | TT | BH1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
36 | TE-BH1060-C1 | TE | BH1060-C1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
65 | TT-BH1060-C2 | TT | BH1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
37 | TE-BH1060-C2 | TE | BH1060-C2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060C OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
25 | PG-PA1060-C | PG | PA1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
30 | SS-BH1060-C | SS | BH1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060C SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
9 | FS-CW1060-D1 | FS | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER FLOW SWITCH(CASING) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
10 | FS-CW1060-D2 | FS | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER FLOW SWITCH(SCREW) | PD-072 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
74 | TT-CW1060-D1 | TT | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER OUTLET TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
75 | TT-CW1060-D2 | TT | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER OUTLET TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-150℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (COOLING SCREW) |  | 0 |  | BOTTOM ASH COOLER
20 | PG-CW1060-D | PG | CW1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
21 | PG-CW1060-D1 | PG | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE(CASING) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
22 | PG-CW1060-D2 | PG | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER PRESSURE GAUGE(SCREW) | PD-072 | - | - | 0~1Mpa | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
57 | TG-CW1060-D | TG | CW1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
58 | TG-CW1060-D1 | TG | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE(CASING) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
59 | TG-CW1060-D2 | TG | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE GAUGE(SCREW) | PD-072 | - | - | 0-150℃ | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
46 | TE-CW1060-D1 | TE | CW1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
47 | TE-CW1060-D2 | TE | CW1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D COOLING WATER TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
66 | TT-BH1060-D1 | TT | BH1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D INLET CHUTE TEMPERATURE TRANSMITTER(CASING) | PD-072 | - | - | 0-1200℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
38 | TE-BH1060-D1 | TE | BH1060-D1 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D INLET CHUTE TEMPERATURE(CASING) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
67 | TT-BH1060-D2 | TT | BH1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D OUTLET CHUTE TEMPERATURE TRANSMITTER(SCREW) | PD-072 | - | - | 0-300℃ | AI 4~20mA | FIELD | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
39 | TE-BH1060-D2 | TE | BH1060-D2 | #1 BOTTOM ASH SCREW CONVEYOR L-1060D OUTLET CHUTE TEMPERATURE(SCREW) | PD-072 | - | - | - | - | FIELD | TT | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
26 | PG-PA1060-C | PG | PA1060-C | #1 BOTTOM ASH SCREW CONVEYOR L-1060D PLANT AIR PRESSURE GAUGE | PD-072 | - | - | later | - | - | - | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
31 | SS-BH1060-D | SS | BH1060-D | #1 BOTTOM ASH SCREW CONVEYOR L-1060D SPEED MONITOR | PD-072 | - | - | - | DI | LCP | DCS | - | PACKAGE (SCREW COOLER) |  | 0 |  | BOTTOM ASH COOLER
36 | ZSE-DO1043-A4 | ZSE | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
20 | SVE-DO1043-A4 | SVE | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 EXTENDING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
43 | ZSR-DO1043-A4 | ZSR | DO1043-A4 | #1 BURNER(A) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
37 | ZSE-DO1043-A5 | ZSE | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
21 | SVE-DO1043-A5 | SVE | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
44 | ZSR-DO1043-A5 | ZSR | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
22 | SVR-DO1043-A5 | SVR | DO1043-A5 | #1 BURNER(A) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
8 | PG-FA1043-A | PG | FA1043-A | #1 BURNER(A) AIR PRESSURE GAUGE | PD-022,2/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
9 | PG-PA1043-A1 | PG | PA1043-A1 | #1 BURNER(A) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,2/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
10 | PG-PA1043-A2 | PG | PA1043-A2 | #1 BURNER(A) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,2/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
14 | PSL-PA1043-A1 | PSL | PA1043-A1 | #1 BURNER(A) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,2/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
12 | PRV-PA1043-A1 | PRV | PA1043-A1 | #1 BURNER(A) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,2/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
29 | ZS1-FA1043-A | ZS1 | FA1043-A | #1 BURNER(A) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
30 | ZS2-FA1043-A | ZS2 | FA1043-A | #1 BURNER(A) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
1 | BT-DO1043-A | BT | DO1043-A | #1 BURNER(A) COMPACT FLAME DETECTOR | PD-022,2/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
3 | FE-DO1043-A | FE | DO1043-A | #1 BURNER(A) DIESEL OIL FLOW ELEMENT | PD-022,2/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
4 | FT-DO1043-A | FT | DO1043-A | #1 BURNER(A) DIESEL OIL FLOW TRANSMITTER | PD-022,2/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
6 | PG-DO1043-A | PG | DO1043-A | #1 BURNER(A) DIESEL OIL PRESSURE GAUGE | PD-022,2/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
13 | PSH-DO1043-A1 | PSH | DO1043-A1 | #1 BURNER(A) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,2/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
15 | PT-DO1043-A2 | PT | DO1043-A2 | #1 BURNER(A) DIESEL OIL PRESSURE TRANSMITTER | PD-022,2/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
7 | PG-DO1043-A2 | PG | DO1043-A2 | #1 BURNER(A) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,2/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
2 | FCV-DO1043-A3 | FCV | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE | PD-022,2/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
28 | ZS-DO1043-A3 | ZS | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
45 | ZT-DO1043-A3 | ZT | DO1043-A3 | #1 BURNER(A) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,2/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
24 | XV-DO1043-A1 | XV | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
31 | ZSC-DO1043-A1 | ZSC | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
16 | SV-DO1043-A1 | SV | DO1043-A1 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
25 | XV-DO1043-A2 | XV | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
32 | ZSC-DO1043-A2 | ZSC | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
39 | ZSO-DO1043-A2 | ZSO | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
17 | SV-DO1043-A2 | SV | DO1043-A2 | #1 BURNER(A) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
11 | PRV-PA1043-A | PRV | PA1043-A | #1 BURNER(A) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,2/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
26 | XV-PA1043-A2 | XV | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
27 | XV-PA1043-A3 | XV | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
18 | SV-PA1043-A2 | SV | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
34 | ZSC-PA1043-A2 | ZSC | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
41 | ZSO-PA1043-A2 | ZSO | PA1043-A2 | #1 BURNER(A) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
19 | SV-PA1043-A3 | SV | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 | PD-022,2/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
35 | ZSC-PA1043-A3 | ZSC | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
42 | ZSO-PA1043-A3 | ZSO | PA1043-A3 | #1 BURNER(A) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
66 | SVE-DO1043-B4 | SVE | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 EXTRENDING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
82 | ZSE-DO1043-B4 | ZSE | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
89 | ZSR-DO1043-B4 | ZSR | DO1043-B4 | #1 BURNER(B) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
67 | SVE-DO1043-B5 | SVE | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 EXTRENDING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
83 | ZSE-DO1043-B5 | ZSE | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
90 | ZSR-DO1043-B5 | ZSR | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
68 | SVR-DO1043-B5 | SVR | DO1043-B5 | #1 BURNER(B) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
54 | PG-FA1043-B | PG | FA1043-B | #1 BURNER(B) AIR PRESSURE GAUGE | PD-022,3/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
55 | PG-PA1043-B1 | PG | PA1043-B1 | #1 BURNER(B) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,3/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
56 | PG-PA1043-B2 | PG | PA1043-B2 | #1 BURNER(B) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,3/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
60 | PSL-PA1043-B1 | PSL | PA1043-B1 | #1 BURNER(B) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,3/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
58 | PRV-PA1043-B1 | PRV | PA1043-B1 | #1 BURNER(B) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,3/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
75 | ZS1-FA1043-B | ZS1 | FA1043-B | #1 BURNER(B) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
76 | ZS2-FA1043-B | ZS2 | FA1043-B | #1 BURNER(B) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
47 | BT-DO1043-B | BT | DO1043-B | #1 BURNER(B) COMPACT FLAME DETECTOR | PD-022,3/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
49 | FE-DO1043-B | FE | DO1043-B | #1 BURNER(B) DIESEL OIL FLOW ELEMENT | PD-022,3/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
50 | FT-DO1043-B | FT | DO1043-B | #1 BURNER(B) DIESEL OIL FLOW TRANSMITTER | PD-022,3/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
52 | PG-DO1043-B | PG | DO1043-B | #1 BURNER(B) DIESEL OIL PRESSURE GAUGE | PD-022,3/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
59 | PSH-DO1043-B1 | PSH | DO1043-B1 | #1 BURNER(B) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,3/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
61 | PT-DO1043-B2 | PT | DO1043-B2 | #1 BURNER(B) DIESEL OIL PRESSURE TRANSMITTER | PD-022,3/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
53 | PG-DO1043-B2 | PG | DO1043-B2 | #1 BURNER(B) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,3/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
48 | FCV-DO1043-B3 | FCV | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE | PD-022,3/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
74 | ZS-DO1043-B3 | ZS | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
91 | ZT-DO1043-B3 | ZT | DO1043-B3 | #1 BURNER(B) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,3/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
70 | XV-DO1043-B1 | XV | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
77 | ZSC-DO1043-B1 | ZSC | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
62 | SV-DO1043-B1 | SV | DO1043-B1 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
71 | XV-DO1043-B2 | XV | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
78 | ZSC-DO1043-B2 | ZSC | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
85 | ZSO-DO1043-B2 | ZSO | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
63 | SV-DO1043-B2 | SV | DO1043-B2 | #1 BURNER(B) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
57 | PRV-PA1043-B | PRV | PA1043-B | #1 BURNER(B) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,3/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
64 | SV-PA1043-B2 | SV | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
65 | SV-PA1043-B3 | SV | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
72 | XV-PA1043-B2 | XV | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
80 | ZSC-PA1043-B2 | ZSC | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
87 | ZSO-PA1043-B2 | ZSO | PA1043-B2 | #1 BURNER(B) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
73 | XV-PA1043-B3 | XV | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 | PD-022,3/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
81 | ZSC-PA1043-B3 | ZSC | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
88 | ZSO-PA1043-B3 | ZSO | PA1043-B3 | #1 BURNER(B) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
128 | ZSE-DO1043-C4 | ZSE | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
135 | ZSR-DO1043-C4 | ZSR | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
112 | SVE-DO1043-C4 | SVE | DO1043-C4 | #1 BURNER(C) 5/2- WAY SOLENOID-1 RETRACTING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
129 | ZSE-DO1043-C5 | ZSE | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
113 | SVE-DO1043-C5 | SVE | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
136 | ZSR-DO1043-C5 | ZSR | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
114 | SVR-DO1043-C5 | SVR | DO1043-C5 | #1 BURNER(C) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
100 | PG-FA1043-C | PG | FA1043-C | #1 BURNER(C) AIR PRESSURE GAUGE | PD-022,4/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
101 | PG-PA1043-C1 | PG | PA1043-C1 | #1 BURNER(C) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,4/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
102 | PG-PA1043-C2 | PG | PA1043-C2 | #1 BURNER(C) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,4/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
106 | PSL-PA1043-C1 | PSL | PA1043-C1 | #1 BURNER(C) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,4/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
104 | PRV-PA1043-C1 | PRV | PA1043-C1 | #1 BURNER(C) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,4/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
121 | ZS1-FA1043-C | ZS1 | FA1043-C | #1 BURNER(C) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
122 | ZS2-FA1043-C | ZS2 | FA1043-C | #1 BURNER(C) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
93 | BT-DO1043-C | BT | DO1043-C | #1 BURNER(C) COMPACT FLAME DETECTOR | PD-022,4/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
95 | FE-DO1043-C | FE | DO1043-C | #1 BURNER(C) DIESEL OIL FLOW ELEMENT | PD-022,4/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
96 | FT-DO1043-C | FT | DO1043-C | #1 BURNER(C) DIESEL OIL FLOW TRANSMITTER | PD-022,4/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
98 | PG-DO1043-C | PG | DO1043-C | #1 BURNER(C) DIESEL OIL PRESSURE GAUGE | PD-022,4/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
105 | PSH-DO1043-C1 | PSH | DO1043-C1 | #1 BURNER(C) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,4/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
107 | PT-DO1043-C2 | PT | DO1043-C2 | #1 BURNER(C) DIESEL OIL PRESSURE TRANSMITTER | PD-022,4/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
99 | PG-DO1043-C2 | PG | DO1043-C2 | #1 BURNER(C) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,4/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
94 | FCV-DO1043-C3 | FCV | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE | PD-022,4/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
120 | ZS-DO1043-C3 | ZS | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
137 | ZT-DO1043-C3 | ZT | DO1043-C3 | #1 BURNER(C) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,4/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
116 | XV-DO1043-C1 | XV | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
123 | ZSC-DO1043-C1 | ZSC | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
108 | SV-DO1043-C1 | SV | DO1043-C1 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
117 | XV-DO1043-C2 | XV | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
124 | ZSC-DO1043-C2 | ZSC | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
131 | ZSO-DO1043-C2 | ZSO | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
109 | SV-DO1043-C2 | SV | DO1043-C2 | #1 BURNER(C) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
103 | PRV-PA1043-C | PRV | PA1043-C | #1 BURNER(C) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,4/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
118 | XV-PA1043-C2 | XV | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
119 | XV-PA1043-C3 | XV | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
110 | SV-PA1043-C2 | SV | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
126 | ZSC-PA1043-C2 | ZSC | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
133 | ZSO-PA1043-C2 | ZSO | PA1043-C2 | #1 BURNER(C) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
111 | SV-PA1043-C3 | SV | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 | PD-022,4/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
127 | ZSC-PA1043-C3 | ZSC | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
134 | ZSO-PA1043-C3 | ZSO | PA1043-C3 | #1 BURNER(C) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
174 | ZSE-DO1043-D4 | ZSE | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 EXTENDED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
181 | ZSR-DO1043-D4 | ZSR | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 RETRACTED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
158 | SVE-DO1043-D4 | SVE | DO1043-D4 | #1 BURNER(D) 5/2- WAY SOLENOID-1 RETRACTING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
175 | ZSE-DO1043-D5 | ZSE | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 EXTENDED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
159 | SVE-DO1043-D5 | SVE | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 EXTENDING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
182 | ZSR-DO1043-D5 | ZSR | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 RETRACTED POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
160 | SVR-DO1043-D5 | SVR | DO1043-D5 | #1 BURNER(D) 5/2- WAY SOLENOID-2 RETRACTING COMMAND | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
146 | PG-FA1043-D | PG | FA1043-D | #1 BURNER(D) AIR PRESSURE GAUGE | PD-022,5/5 | 0.21 | 350 | -0.01~0.05Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
147 | PG-PA1043-D1 | PG | PA1043-D1 | #1 BURNER(D) ATOMIZING AIR PRESSURE GAUGE-1 | PD-022,5/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
148 | PG-PA1043-D2 | PG | PA1043-D2 | #1 BURNER(D) ATOMIZING AIR PRESSURE GAUGE-2 | PD-022,5/5 | 10 | 50 | 0~10Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
152 | PSL-PA1043-D1 | PSL | PA1043-D1 | #1 BURNER(D) ATOMIZING AIR PRESSURE LOW SWITCH | PD-022,5/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
150 | PRV-PA1043-D1 | PRV | PA1043-D1 | #1 BURNER(D) ATOMIZING/PURGING AIR PRESSURE REGULATOR VALVE | PD-022,5/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
167 | ZS1-FA1043-D | ZS1 | FA1043-D | #1 BURNER(D) COMBUSTION AIR DAMPER IN IGNITING POSITION | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
168 | ZS2-FA1043-D | ZS2 | FA1043-D | #1 BURNER(D) COMBUSTION AIR DAMPER IN PURGE POSITION | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
139 | BT-DO1043-D | BT | DO1043-D | #1 BURNER(D) COMPACT FLAME DETECTOR | PD-022,5/5 | - | - | - | WET AI 4~20mA | LCP | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
141 | FE-DO1043-D | FE | DO1043-D | #1 BURNER(D) DIESEL OIL FLOW ELEMENT | PD-022,5/5 | 10 | 50 | 0~3500Kg/H | - | - | - | CORIOLIS | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
142 | FT-DO1043-D | FT | DO1043-D | #1 BURNER(D) DIESEL OIL FLOW TRANSMITTER | PD-022,5/5 | 15 | 50 | 0~3500Kg/H | WET AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
144 | PG-DO1043-D | PG | DO1043-D | #1 BURNER(D) DIESEL OIL PRESSURE GAUGE | PD-022,5/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
151 | PSH-DO1043-D1 | PSH | DO1043-D1 | #1 BURNER(D) DIESEL OIL PRESSURE HIGH SWITCH | PD-022,5/5 | 10 | 50 | 0.5~6Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
153 | PT-DO1043-D2 | PT | DO1043-D2 | #1 BURNER(D) DIESEL OIL PRESSURE TRANSMITTER | PD-022,5/5 | 15 | 50 | 0~6Kg/c㎡G | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
145 | PG-DO1043-D2 | PG | DO1043-D2 | #1 BURNER(D) DIESEL OIL SUPPLY PRESSURE GAUGE | PD-022,5/5 | 15 | 50 | 0~25.5Kg/c㎡G | - | - | - | - | PACKAGE (BURNER) |  | 1 | OK | DIESEL OIL AND BURNER
177 | ZSO-DO1043-D2 | ZSO | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
140 | FCV-DO1043-D3 | FCV | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE | PD-022,5/5 | - | - | - | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
166 | ZS-DO1043-D3 | ZS | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE IN IGNITION POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
183 | ZT-DO1043-D3 | ZT | DO1043-D3 | #1 BURNER(D) FUEL OIL CONTROL VALVE POSITION TRANSMITTER | PD-022,5/5 | - | - | - | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
162 | XV-DO1043-D1 | XV | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
169 | ZSC-DO1043-D1 | ZSC | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
154 | SV-DO1043-D1 | SV | DO1043-D1 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-1 SOLENOID VALVE | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
163 | XV-DO1043-D2 | XV | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
155 | SV-DO1043-D2 | SV | DO1043-D2 | #1 BURNER(D) FUEL OIL PNEUMATIC VALVE-2 SOLENOID VALVE | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
170 | ZSC-DO1043-D2 | ZSC | DO1043-D2 | #1 BURNER(D) FUEL OILPNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
149 | PRV-PA1043-D | PRV | PA1043-D | #1 BURNER(D) PLANT AIR PRESSURE REGULATOR VALVE | PD-022,5/5 | 10 | 50 | 7.1~4Kg/c㎡G | - | - | - | - | FHI |  | 1 |  | DIESEL OIL AND BURNER
164 | XV-PA1043-D2 | XV | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
165 | XV-PA1043-D3 | XV | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 | PD-022,5/5 | - | - | - | - | - | - | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
156 | SV-PA1043-D2 | SV | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
157 | SV-PA1043-D3 | SV | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-1 | PD-022,5/5 | - | - | - | DO | DCS | FIELD | 24VDC | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
172 | ZSC-PA1043-D2 | ZSC | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
179 | ZSO-PA1043-D2 | ZSO | PA1043-D2 | #1 BURNER(D) PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
173 | ZSC-PA1043-D3 | ZSC | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
180 | ZSO-PA1043-D3 | ZSO | PA1043-D3 | #1 BURNER(D) PNEUMATIC VALVE-2 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
42 | LSH-CH1105 | LSH | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
41 | LSL-CH1105 | LSL | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
40 | LSLL-CH1105 | LSLL | CH1105 | #1 CARBON HYDRARIDE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
13 | LS-CL1061-C4 | LS | CL1061-C4 | #1 C-COAL FEEDER BELT TRACKING SWITCH-1 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
14 | LS-CL1061-C5 | LS | CL1061-C5 | #1 C-COAL FEEDER BELT TRACKING SWITCH-2 | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
15 | LS-CL1061-C6 | LS | CL1061-C6 | #1 C-COAL FEEDER CHUTE PLUGGING SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
3 | FT-CL1061-C | FT | CL1061-C | #1 C-COAL FEEDER COAL FLOW MONITOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
25 | PS-IA1061-C1 | PS | IA1061-C1 | #1 C-COAL FEEDER IA PRESSURE HIGH SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
27 | PS-IA1061-C2 | PS | IA1061-C2 | #1 C-COAL FEEDER IA PRESSURE LOW SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
52 | ZSC-CL1061-C1 | ZSC | CL1061-C1 | #1 C-COAL FEEDER INLET VALVE-1 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
61 | ZSO-CL1061-C1 | ZSO | CL1061-C1 | #1 C-COAL FEEDER INLET VALVE-1 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
53 | ZSC-CL1061-C2 | ZSC | CL1061-C2 | #1 C-COAL FEEDER INLET VALVE-2 CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
62 | ZSO-CL1061-C2 | ZSO | CL1061-C2 | #1 C-COAL FEEDER INLET VALVE-2 OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
41 | WT-CL1061-C1 | WT | CL1061-C1 | #1 C-COAL FEEDER LOAD CELL-1 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
42 | WT-CL1061-C2 | WT | CL1061-C2 | #1 C-COAL FEEDER LOAD CELL-2 | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
12 | LS-CL1061-C3 | LS | CL1061-C3 | #1 C-COAL FEEDER NO COAL SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
45 | XV-CL1061-C7 | XV | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
54 | ZSC-CL1061-C7 | ZSC | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE CLOSE POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
63 | ZSO-CL1061-C7 | ZSO | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE OPEN POSITION SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
33 | SV-CL1061-C7 | SV | CL1061-C7 | #1 C-COAL FEEDER OUTLET VALVE SOLENOID VALVE | PD-061 | - | - | - | DO | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
30 | SE-CL1061-C | SE | CL1061-C | #1 C-COAL FEEDER SPEED DETECTOR | PD-061 | - | - | - | AI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
36 | TS-CL1061-C | TS | CL1061-C | #1 C-COAL FEEDER THERMO SWITCH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | NEW ADDED | 1 |  | COAL FEEDER
115 | PG-CH1109A | PG | CH1109A | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE DOSING PUMP Z-1109A DISCHARGE PRESSURE GAUGE | PD-042 | 12.24 | 35 | 0~20 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
116 | PG-CH1109B | PG | CH1109B | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE DOSING PUMP Z-1109B DISCHARGE PRESSURE GAUGE | PD-042 | 12.24 | 35 | 0~20 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
35 | LG-CH1105 | LG | CH1105 | #1 CHEMICAL DOSING SYSTEM CARBON HYDRARIDE SOLUTION TANK Z-1105 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
32 | LG-CH1102 | LG | CH1102 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1102 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
34 | LG-CH1104 | LG | CH1104 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1104 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
36 | LG-CH1106 | LG | CH1106 | #1 CHEMICAL DOSING SYSTEM MEASUREING VESSEL Z-1106 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
113 | PG-CH1108A | PG | CH1108A | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE DOSING PUMP Z-1108A DISCHARGE PRESSURE GAUGE | PD-042 | 18.36 | 35 | 0~40 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
114 | PG-CH1108B | PG | CH1108B | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE DOSING PUMP Z-1108B DISCHARGE PRESSURE GAUGE | PD-042 | 18.36 | 35 | 0~40 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
33 | LG-CH1103 | LG | CH1103 | #1 CHEMICAL DOSING SYSTEM NEUTRAL AMINE SOLUTION TANK Z-1103 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
111 | PG-CH1107A | PG | CH1107A | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE DOSING PUMP Z-1107A DISCHARGE PRESSURE GAUGE | PD-042 | 184.62 | 35 | 0~250 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
112 | PG-CH1107B | PG | CH1107B | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE DOSING PUMP Z-1107B DISCHARGE PRESSURE GAUGE | PD-042 | 184.62 | 35 | 0~250 | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | PG
31 | LG-CH1101 | LG | CH1101 | #1 CHEMICAL DOSING SYSTEM TRI-SODIUM PHOSPHATE SOLUTION TANK Z-1101 LEVEL GAUGE | PD-042 | - | - | - | - | - | - | - | PACKAGE (CHEMICAL DOSING) | NEW ADDED | 0 |  | LG
1 | PG-PA1066A~I | PG | PA1066A~I | #1 COAL BUNKER A (T-1008A) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
4 | SV-PA1066A~I | SV | PA1066A~I | #1 COAL BUNKER A (T-1008A) AIR CANNON SOLENOID VALVE SV-PA1066A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
2 | PG-PA1067A~I | PG | PA1067A~I | #1 COAL BUNKER B (T-1008B) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
5 | SV-PA1067A~I | SV | PA1067A~I | #1 COAL BUNKER B (T-1008B) AIR CANNON SOLENOID VALVE SV-PA1067A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
3 | PG-PA1068A~I | PG | PA1068A~I | #1 COAL BUNKER C (T-1008C) AIR CANNON PRESSURE GAUGE A~I | - | - | - | 0~10Kg/cm2G | - | - | - | - | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
6 | SV-PA1068A~I | SV | PA1068A~I | #1 COAL BUNKER C (T-1008C) AIR CANNON SOLENOID VALVE SV-PA1068A~I | - | - | - | - | DO | FIELD | LCP | 110Vac | PACKAGE (AIR CANNON) | NEW ADDED | 1 |  | AIR CANNON
29 | FE-FA1061-A3 | FE | FA1061-A3 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
30 | FE-FA1061-A4 | FE | FA1061-A4 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
40 | FG-FA1061-A3 | FG | FA1061-A3 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
41 | FG-FA1061-A4 | FG | FA1061-A4 | #1 COAL FEEDER (A) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
28 | FE-FA1061-A2 | FE | FA1061-A2 | #1 COAL FEEDER (A) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
39 | FG-FA1061-A2 | FG | FA1061-A2 | #1 COAL FEEDER (A) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
27 | FE-FA1061-A1 | FE | FA1061-A1 | #1 COAL FEEDER (A) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
38 | FG-FA1061-A1 | FG | FA1061-A1 | #1 COAL FEEDER (A) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
33 | FE-FA1061-B3 | FE | FA1061-B3 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
34 | FE-FA1061-B4 | FE | FA1061-B4 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
44 | FG-FA1061-B3 | FG | FA1061-B3 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
45 | FG-FA1061-B4 | FG | FA1061-B4 | #1 COAL FEEDER (B) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
32 | FE-FA1061-B2 | FE | FA1061-B2 | #1 COAL FEEDER (B) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
43 | FG-FA1061-B2 | FG | FA1061-B2 | #1 COAL FEEDER (B) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
31 | FE-FA1061-B1 | FE | FA1061-B1 | #1 COAL FEEDER (B) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
42 | FG-FA1061-B1 | FG | FA1061-B1 | #1 COAL FEEDER (B) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
37 | FE-FA1061-C3 | FE | FA1061-C3 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW ELEMENT-1 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
38 | FE-FA1061-C4 | FE | FA1061-C4 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW ELEMENT-2 | PD-061 | -340~2500 mmH2O | 343 | 0~7 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
48 | FG-FA1061-C3 | FG | FA1061-C3 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW GAUGE-1 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
49 | FG-FA1061-C4 | FG | FA1061-C4 | #1 COAL FEEDER (C) OUTLET HOT AIR FLOW GAUGE-2 | PD-061 | -340~2500 mmH2O | 343 | 0~6 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
36 | FE-FA1061-C2 | FE | FA1061-C2 | #1 COAL FEEDER (C) OUTLET PURGE AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
47 | FG-FA1061-C2 | FG | FA1061-C2 | #1 COAL FEEDER (C) OUTLET PURGE AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~0.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
35 | FE-FA1061-C1 | FE | FA1061-C1 | #1 COAL FEEDER (C) SEALING AIR FLOW ELEMENT | PD-061 | -340~2500 mmH2O | 80 | 0~1.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
46 | FG-FA1061-C1 | FG | FA1061-C1 | #1 COAL FEEDER (C) SEALING AIR FLOW GAUGE | PD-061 | -340~2500 mmH2O | 80 | 0~1.2 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
16 | PS-IA1061-A1 | PS | IA1061-A1 | #1 COAL FEEDER A INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
18 | PS-IA1061-A2 | PS | IA1061-A2 | #1 COAL FEEDER A INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
20 | PS-IA1061-B1 | PS | IA1061-B1 | #1 COAL FEEDER B INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
22 | PS-IA1061-B2 | PS | IA1061-B2 | #1 COAL FEEDER B INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
24 | PS-IA1061-C1 | PS | IA1061-C1 | #1 COAL FEEDER C INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
26 | PS-IA1061-C2 | PS | IA1061-C2 | #1 COAL FEEDER C INSTRUMENT AIR PRESSURE SWITCH LOW | PD-061 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) |  | 1 |  | COAL FEEDER
7 | PS-IA1061-D1 | PS | IA1061-D1 | #1 COAL FEEDER D INSTRUMENT AIR PRESSURE SWITCH HIGH | PD-052 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | DELETED 20150529 | 1 |  | COAL FEEDER
8 | PS-IA1061-D2 | PS | IA1061-D2 | #1 COAL FEEDER D INSTRUMENT AIR PRESSURE SWITCH LOW | PD-052 | - | - | - | DI | FIELD | LCP | - | PACKAGE (COAL FEEDER) | DELETED 20150529 | 1 |  | COAL FEEDER
44 | LSH-CL1008-A | LSH | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
43 | LSL-CL1008-A | LSL | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
29 | LT-CL1008-A | LT | CL1008-A | #1 COAL SILO (A) T-1008A LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
46 | LSH-CL1008-B | LSH | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
45 | LSL-CL1008-B | LSL | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
30 | LT-CL1008-B | LT | CL1008-B | #1 COAL SILO (B) T-1008B LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
48 | LSH-CL1008-C | LSH | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL HIGH SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
47 | LSL-CL1008-C | LSL | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL LOW SWITCH | PD-061 | ±254 mmH2O | 80 | - | DI | FIELD | DCS | VIBRATION | FHI |  | 0 |  | LS
31 | LT-CL1008-C | LT | CL1008-C | #1 COAL SILO (C) T-1008C LEVEL TRANSMITTER | PD-061 | ±254 mmH2O | 80 | 0.5~20 M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
21 | ZSF-SB1042 | ZSF | SB1042 | #1 COLD END SOOTBLOWER LANCE EXTEND LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
23 | ZSR-SB1042 | ZSR | SB1042 | #1 COLD END SOOTBLOWER LANCE PARK LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
5 | PT-SB1042 | PT | SB1042 | #1 COLD END SOOTBLOWER STEAM PRESSURE TRANSMITTER | - | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
5 | PT-CR1003 | PT | CR1003 | #1 COLD REHEAT STEAM PRESSURE TRANSMITTER | PD-012 | 45 | 395 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
19 | TW-CR1004 | TW | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
16 | TE-CR1004 | TE | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
6 | TT-CR1004 | TT | CR1004 | #1 COLD REHEAT STEAM TEMPERATURE TRANSMITTER | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
6 | PCV-AS1020-2 | PCV | AS1020-2 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE (HIGH LOAD) | PD-014 | 45 | 395 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
5 | PCV-AS1020-1 | PCV | AS1020-1 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE (LOW LOAD) | PD-014 | 45 | 395 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
27 | ZT-AS1020-2 | ZT | AS1020-2 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER (HIGH LOAD) | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
26 | ZT-AS1020-1 | ZT | AS1020-1 | #1 COLD REHEAT TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER (LOW LOAD) | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
1 | XV-CR1011 | XV | CR1011 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 DRAIN VALVE | PD-011 | 45 | 395 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
1 | LS-CR1001-1 | LS | CR1001-1 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 HIGH LEVEL SWITCH | PD-011 | 45 | 395 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
2 | LS-CR1001-2 | LS | CR1001-2 | #1 COLD REHEATER LINE A DRAIN POT DP-CR01 HIGH-HIGH LEVEL SWITCH | PD-011 | 45 | 395 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
2 | XV-CR1012 | XV | CR1012 | #1 COLD REHEATER LINE B DRAIN POT DP-CR02 DRAIN VALVE | PD-011 | 45 | 395 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
4 | ZSC-CR1011 | ZSC | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
5 | ZSO-CR1011 | ZSO | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
1 | SV-CR1011 | SV | CR1011 | #1 COLD REHEATER LINE DRAIN POT DP-CR01 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
6 | ZSC-CR1012 | ZSC | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
2 | SV-CR1012 | SV | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
7 | ZSO-CR1012 | ZSO | CR1012 | #1 COLD REHEATER LINE DRAIN POT DP-CR02 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
13 | LCV-MU1110 | LCV | MU1110 | #1 CONDENER MAKEUP WATER LEVEL CONTROL VALVE | PD-016 | 10 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
49 | ZT-MU1110 | ZT | MU1110 | #1 CONDENER MAKEUP WATER LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
44 | TE-CD1116-A1 | TE | CD1116-A1 | #1 CONDENSAT PUMP (A) COUPLING TEMPERATURE ELEMENT | PD-016 | - | - | 0~120 | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
33 | TT-CD1116-A1 | TT | CD1116-A1 | #1 CONDENSAT PUMP (A) COUPLING TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
46 | TE-CD1116-A4 | TE | CD1116-A4 | #1 CONDENSAT PUMP (A) MOTOR BEARING NON-DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
35 | TT-CD1116-A4 | TT | CD1116-A4 | #1 CONDENSAT PUMP (A) MOTOR BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
45 | TE-CD1116-A3 | TE | CD1116-A3 | #1 CONDENSAT PUMP (A) MOTOR BEARING DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
34 | TT-CD1116-A3 | TT | CD1116-A3 | #1 CONDENSAT PUMP (A) MOTOR BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
47 | TE-CD1116-AU1 | TE | CD1116-AU1 | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
48 | TE-CD1116-AU2 | TE | CD1116-AU2 | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
36 | TT-CD1116-AU | TT | CD1116-AU | #1 CONDENSAT PUMP (A) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
49 | TE-CD1116-AV1 | TE | CD1116-AV1 | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
50 | TE-CD1116-AV2 | TE | CD1116-AV2 | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
37 | TT-CD1116-AV | TT | CD1116-AV | #1 CONDENSAT PUMP (A) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
51 | TE-CD1116-AW1 | TE | CD1116-AW1 | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
52 | TE-CD1116-AW2 | TE | CD1116-AW2 | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
38 | TT-CD1116-AW | TT | CD1116-AW | #1 CONDENSAT PUMP (A) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
53 | TE-CD1116-B1 | TE | CD1116-B1 | #1 CONDENSAT PUMP (B) COUPLING TEMPERATURE ELEMENT | PD-016 | - | - | 0~120 | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
39 | TT-CD1116-B1 | TT | CD1116-B1 | #1 CONDENSAT PUMP (B) COUPLING TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
54 | TE-CD1116-B3 | TE | CD1116-B3 | #1 CONDENSAT PUMP (B) MOTOR BEARING DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
40 | TT-CD1116-B3 | TT | CD1116-B3 | #1 CONDENSAT PUMP (B) MOTOR BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
55 | TE-CD1116-B4 | TE | CD1116-B4 | #1 CONDENSAT PUMP (B) MOTOR BEARING NON-DRIVEN END TEMPERATURE ELEMENT | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
41 | TT-CD1116-B4 | TT | CD1116-B4 | #1 CONDENSAT PUMP (B) MOTOR BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-016 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
56 | TE-CD1116-BU1 | TE | CD1116-BU1 | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
57 | TE-CD1116-BU2 | TE | CD1116-BU2 | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
42 | TT-CD1116-BU | TT | CD1116-BU | #1 CONDENSAT PUMP (B) MOTOR WINDING U TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
58 | TE-CD1116-BV1 | TE | CD1116-BV1 | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
59 | TE-CD1116-BV2 | TE | CD1116-BV2 | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
43 | TT-CD1116-BV | TT | CD1116-BV | #1 CONDENSAT PUMP (B) MOTOR WINDING V TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
60 | TE-CD1116-BW1 | TE | CD1116-BW1 | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-1 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
61 | TE-CD1116-BW2 | TE | CD1116-BW2 | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE ELEMENT-2 | PD-016 | - | - | - | - | FIELD | TT | RTD | PACKAGE (CONDENSATE PUMP) |  | 0 |  | TE
44 | TT-CD1116-BW | TT | CD1116-BW | #1 CONDENSAT PUMP (B) MOTOR WINDING W TEMPERATURE TRANSMITTER | PD-016 | - | - | 0-200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
131 | PG-CD1716A | PG | CD1716A | #1 CONDENSATE BOOSTER PUMP P-1716A DISCHARGE PRESSURE GAUGE | PD-047 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
132 | PG-CD1716B | PG | CD1716B | #1 CONDENSATE BOOSTER PUMP P-1716B DISCHARGE PRESSURE GAUGE | PD-047 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI | NEW ADDED | 0 |  | PG
12 | LCV-CD1110 | LCV | CD1110 | #1 CONDENSATE DUMPING VALVE TO RAW WATER PIT LEVEL CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
42 | ZT-CD1110 | ZT | CD1110 | #1 CONDENSATE DUMPING VALVE TO RAW WATER PIT LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
10 | FCV-CD1121 | FCV | CD1121 | #1 CONDENSATE POLISHIER FLOW CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
45 | ZT-CD1121 | ZT | CD1121 | #1 CONDENSATE POLISHIER FLOW CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
95 | TG-CD1116-A | TG | CD1116-A | #1 CONDENSATE PUMP (A) COUPLING TEMPERATURE DAUGE | PD-016 | - | - | later | - | - | - | - | PACKAGE (CONDENSATE PUMP) | DELETED | 0 |  | TG
3 | VT-CD1116-A3 | VT | CD1116-A3 | #1 CONDENSATE PUMP (A) MOTOR DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
4 | VT-CD1116-A4 | VT | CD1116-A4 | #1 CONDENSATE PUMP (A) MOTOR NON-DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
1 | VT-CD1116-A1 | VT | CD1116-A1 | #1 CONDENSATE PUMP (A) VIBRATION TRANSMITTER-1 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
2 | VT-CD1116-A2 | VT | CD1116-A2 | #1 CONDENSATE PUMP (A) VIBRATION TRANSMITTER-2 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
96 | TG-CD1116-B | TG | CD1116-B | #1 CONDENSATE PUMP (B) COUPLING TEMPERATURE DAUGE | PD-016 | - | - | later | - | - | - | - | PACKAGE (CONDENSATE PUMP) | DELETED | 0 |  | TG
7 | VT-CD1116-B3 | VT | CD1116-B3 | #1 CONDENSATE PUMP (B) MOTOR DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
8 | VT-CD1116-B4 | VT | CD1116-B4 | #1 CONDENSATE PUMP (B) MOTOR NON-DRIVEN END VIBRATION TRANSMITTER | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) |  | 0 |  | VT
5 | VT-CD1116-B1 | VT | CD1116-B1 | #1 CONDENSATE PUMP (B) VIBRATION TRANSMITTER-1 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
6 | VT-CD1116-B2 | VT | CD1116-B2 | #1 CONDENSATE PUMP (B) VIBRATION TRANSMITTER-2 | PD-016 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (CONDENSATE PUMP) | RESERVED 20150408 | 0 |  | VT
20 | PG-CD1116-A2 | PG | CD1116-A2 | #1 CONDENSATE PUMP A DISCHARGE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
19 | PG-CD1116-A1 | PG | CD1116-A1 | #1 CONDENSATE PUMP A SUCTION PRESSURE GAUGE | PD-016 | 3.5 | 65 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
1 | DPT-CD1001 | DPT | CD1001 | #1 CONDENSATE PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-016 | 3.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | DPT
22 | PG-CD1116-B2 | PG | CD1116-B2 | #1 CONDENSATE PUMP B DISCHARGE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
21 | PG-CD1116-B1 | PG | CD1116-B1 | #1 CONDENSATE PUMP B SUCTION PRESSURE GAUGE | PD-016 | 3.5 | 65 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
2 | DPT-CD1002 | DPT | CD1002 | #1 CONDENSATE PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-016 | 3.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | DPT
20 | AT-SP1020 | AT | SP1020 | #1 CONDENSATE PUMP OUTLET WATER SODIUM | PD-044 | 24 | 65.6 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
20 | FG-SP1018 | FG | SP1018 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR 1st CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
21 | FG-SP1019 | FG | SP1019 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR 2nd CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
22 | FG-SP1020 | FG | SP1020 | #1 CONDENSATE PUMP OUTLET FLOWMETER FOR SODIUM ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
128 | PG-SP1008 | PG | SP1008 | #1 CONDENSATE PUMP OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
94 | TG-SP1008 | TG | SP1008 | #1 CONDENSATE PUMP OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
18 | AT-SP1018 | AT | SP1018 | #1 CONDENSATE PUMP OUTLET WATER CATION CONDUCTIVITY-1 | PD-044 | 24 | 65.6 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
19 | AT-SP1019 | AT | SP1019 | #1 CONDENSATE PUMP OUTLET WATER CATION CONDUCTIVITY-2 | PD-044 | 24 | 65.6 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
9 | FCV-CD1120 | FCV | CD1120 | #1 CONDENSATE SYSTEM MINIMUM FLOW RECIRCULATION CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
44 | ZT-CD1120 | ZT | CD1120 | #1 CONDENSATE SYSTEM MINIMUM FLOW RECIRCULATION CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
31 | MV-CD1007 | MV | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
121 | ZSC-CD1007 | ZSC | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
122 | ZSO-CD1007 | ZSO | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
39 | ZT-CD1007 | ZT | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
123 | TS-CD1007 | TS | CD1007 | #1 CONDENSATE TO POLISHER SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
3 | FE-CD1120 | FE | CD1120 | #1 CONDENSATE WATER FLOW ELEMENT | PD-016 | 24 | 65 | 0~400 | <5000 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
3 | FT-CD1120 | FT | CD1120 | #1 CONDENSATE WATER FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
23 | PG-CD1117 | PG | CD1117 | #1 CONDENSATE WATER PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
4 | PS-CD1117 | PS | CD1117 | #1 CONDENSATE WATER PRESSURE LOW SWITCH | PD-016 | 24 | 65 | 15.5 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
20 | PT-CD1117 | PT | CD1117 | #1 CONDENSATE WATER PRESSURE TRANSMITTER | PD-016 | 24 | 65 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
70 | TW-CD1118 | TW | CD1118 | #1 CONDENSATE WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
62 | TE-CD1118 | TE | CD1118 | #1 CONDENSATE WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
71 | TW-CD1118(G) | TW | CD1118(G) | #1 CONDENSATE WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
17 | TG-CD1118 | TG | CD1118 | #1 CONDENSATE WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
45 | TT-CD1118 | TT | CD1118 | #1 CONDENSATE WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
12 | XV-CD1006 | XV | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
119 | ZSC-CD1006 | ZSC | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
120 | ZSO-CD1006 | ZSO | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
14 | SV-CD1006 | SV | CD1006 | #1 CONDENSER CURTAIN SPRAY CONTROL VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
69 | TW-CD1110-4 | TW | CD1110-4 | #1 CONDENSER FLASH CHAMBER TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
43 | TE-CD1110-4 | TE | CD1110-4 | #1 CONDENSER FLASH CHAMBER TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
67 | TW-CD1110-2(G) | TW | CD1110-2(G) | #1 CONDENSER FLASH CHAMBER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
16 | TG-CD1110-2 | TG | CD1110-2 | #1 CONDENSER FLASH CHAMBER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
32 | TT-CD1110-4 | TT | CD1110-4 | #1 CONDENSER FLASH CHAMBERTEMPERATURE TRANSMITTER | PD-016 | 1.03 & Full Vacuum | 120 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
64 | TW-CD1110-1 | TW | CD1110-1 | #1 CONDENSER HOT WELL STEAM TEMPERATURE ELEMENT-1 | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
40 | TE-CD1110-1 | TE | CD1110-1 | #1 CONDENSER HOT WELL STEAM TEMPERATURE ELEMENT-1 | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
2 | LG-CD1110 | LG | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL GAUGE | PD-016 | Full Vaccum & 1.03 | 120 | 0~600 | - | - | - | REFLEX | FHI |  | 0 |  | LG
4 | LT-CD1110 | LT | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL TRANSMITTER | PD-016 | Full Vaccum & 1.03 | 120 | 0~900 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
5 | LSHH-CD1110 | LSHH | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL(HIGH-HIGH) SWITCH | PD-016 | Full Vaccum & 1.03 | 120 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
4 | LSLL-CD1110 | LSLL | CD1110 | #1 CONDENSER HOT WELL WATER LEVEL(LOW-LOW) SWITCH | PD-016 | Full Vaccum & 1.03 | 120 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
66 | TW-CD1110-2 | TW | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE ELEMENT-2 | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
41 | TE-CD1110-2 | TE | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE ELEMENT-2 | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
65 | TW-CD1110-1(G) | TW | CD1110-1(G) | #1 CONDENSER HOT WELL WATER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
15 | TG-CD1110-1 | TG | CD1110-1 | #1 CONDENSER HOT WELL WATER TEMPERATURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
29 | TT-CD1110-1 | TT | CD1110-1 | #1 CONDENSER HOT WELL WATER TEMPERATURE TRANSMITTER-1 | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
30 | TT-CD1110-2 | TT | CD1110-2 | #1 CONDENSER HOT WELL WATER TEMPERATURE TRANSMITTER-2 | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
61 | PG-SW1110-A1 | PG | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
31 | PT-SW1110-A1 | PT | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
121 | TW-SW1110-A1 | TW | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
107 | TE-SW1110-A1 | TE | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
122 | TW-SW1110-A1(G) | TW | SW1110-A1(G) | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
50 | TG-SW1110-A1 | TG | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
84 | TT-SW1110-A1 | TT | SW1110-A1 | #1 CONDENSER INLET (A) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
63 | PG-SW1110-B1 | PG | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
33 | PT-SW1110-B1 | PT | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
125 | TW-SW1110-B1 | TW | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
109 | TE-SW1110-B1 | TE | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
126 | TW-SW1110-B1(G) | TW | SW1110-B1(G) | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
52 | TG-SW1110-B1 | TG | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
86 | TT-SW1110-B1 | TT | SW1110-B1 | #1 CONDENSER INLET (B) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
68 | TW-CD1110-3 | TW | CD1110-3 | #1 CONDENSER NECK TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
42 | TE-CD1110-3 | TE | CD1110-3 | #1 CONDENSER NECK TEMPERATURE ELEMENT | PD-016 | 1.03 | 120 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
31 | TT-CD1110-3 | TT | CD1110-3 | #1 CONDENSER NECK TEMPERATURE TRANSMITTER | PD-016 | 1.055 & Full Vacuum | 100 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
62 | PG-SW1110-A2 | PG | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
32 | PT-SW1110-A2 | PT | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
123 | TW-SW1110-A2 | TW | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
108 | TE-SW1110-A2 | TE | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
124 | TW-SW1110-A2(G) | TW | SW1110-A2(G) | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
51 | TG-SW1110-A2 | TG | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
85 | TT-SW1110-A2 | TT | SW1110-A2 | #1 CONDENSER OUTLET (A) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
64 | PG-SW1110-B2 | PG | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
34 | PT-SW1110-B2 | PT | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER PRESSURE TRANSMITTER | PD-020 | 5 | 50 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
127 | TW-SW1110-B2 | TW | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
110 | TE-SW1110-B2 | TE | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE ELEMENT | PD-020 | 5 | 50 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
128 | TW-SW1110-B2(G) | TW | SW1110-B2(G) | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
53 | TG-SW1110-B2 | TG | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
87 | TT-SW1110-B2 | TT | SW1110-B2 | #1 CONDENSER OUTLET (B) PATH SEAWATER TEMPERATURE TRANSMITTER | PD-020 | 5 | 50 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
18 | PG-CD1110 | PG | CD1110 | #1 CONDENSER PRESSURE GAUGE | PD-016 | 1.055 & Full Vaccum | 100 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
1 | PS-CD1110-1 | PS | CD1110-1 | #1 CONDENSER PRESSURE SWITCH-1 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
2 | PS-CD1110-2 | PS | CD1110-2 | #1 CONDENSER PRESSURE SWITCH-2 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
3 | PS-CD1110-3 | PS | CD1110-3 | #1 CONDENSER PRESSURE SWITCH-3 | PD-016 | 1.055 & Full Vaccum | 100 | -0.8 | DI | FIELD | DCS | BOURDON | FHI |  | 0 |  | PS
19 | PT-CD1110 | PT | CD1110 | #1 CONDENSER PRESSURE TRANSMITTER | PD-016 | 1.055 & Full Vaccum | 100 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
48 | MV-AV1391 | MV | AV1391 | #1 CONDENSER VACUUM BREAKER MOV | PD-027 | 1.5 | 120 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
206 | ZSC-AV1391 | ZSC | AV1391 | #1 CONDENSER VACUUM BREAKER MOV CLOSE POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
207 | ZSO-AV1391 | ZSO | AV1391 | #1 CONDENSER VACUUM BREAKER MOV OPEN POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
80 | ZT-AV1391 | ZT | AV1391 | #1 CONDENSER VACUUM BREAKER MOV POSITION TRANSMITTER | PD-027 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
208 | TS-AV1391 | TS | AV1391 | #1 CONDENSER VACUUM BREAKER MOV TORQUE SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
13 | XV-CD1104-2 | XV | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER | PD-016 | 8 | 170 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
127 | ZSC-CD1104-2 | ZSC | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
128 | ZSO-CD1104-2 | ZSO | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
15 | SV-CD1104-2 | SV | CD1104-2 | #1 CONDESATE EMERGENCY DRAIN VALVE TO CONDENSER SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
4 | FE-CD1121 | FE | CD1121 | #1 CONDESATE POLISHER SYSTEM INLET FLOW ELEMENT | PD-016 | 24 | 65 | 0~200 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
4 | FT-CD1121 | FT | CD1121 | #1 CONDESATE POLISHER SYSTEM INLET FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~200 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
184 | TW-FG1092-A | TW | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
180 | TE-FG1092-A | TE | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
143 | TT-FG1092-A | TT | FG1092-A | #1 CYCLONE A INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
186 | TW-FG1095-A | TW | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
182 | TE-FG1095-A | TE | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
188 | TW-FG1096-A | TW | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
184 | TE-FG1096-A | TE | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
145 | TT-FG1095-A | TT | FG1095-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE-1 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
147 | TT-FG1096-A | TT | FG1096-A | #1 CYCLONE A OUTLET FLUE GAS TEMPERATURE-2 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
56 | PT-FG1009-A1 | PT | FG1009-A1 | #1 CYCLONE A SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
57 | PT-FG1009-A2 | PT | FG1009-A2 | #1 CYCLONE A SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
24 | FE-FA1009-A2 | FE | FA1009-A2 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT B | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
34 | FG-FA1009-A1 | FG | FA1009-A1 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE A | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
35 | FG-FA1009-A2 | FG | FA1009-A2 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE B | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
23 | FE-FA1009-A1 | FE | FA1009-A1 | #1 CYCLONE A SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT A | PD-054,2/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
163 | TW-FG1009-A | TW | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
159 | TE-FG1009-A | TE | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
115 | TT-FG1009-A | TT | FG1009-A | #1 CYCLONE A SEAL POT TEMPERATURE TEMPERATURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
185 | TW-FG1092-B | TW | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
181 | TE-FG1092-B | TE | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
144 | TT-FG1092-B | TT | FG1092-B | #1 CYCLONE B INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
187 | TW-FG1095-B | TW | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
183 | TE-FG1095-B | TE | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-1 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
189 | TW-FG1096-B | TW | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
185 | TE-FG1096-B | TE | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE ELEMENT-2 | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
146 | TT-FG1095-B | TT | FG1095-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE-1 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
148 | TT-FG1096-B | TT | FG1096-B | #1 CYCLONE B OUTLET FLUE GAS TEMPERATURE-2 TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
58 | PT-FG1009-B1 | PT | FG1009-B1 | #1 CYCLONE B SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
59 | PT-FG1009-B2 | PT | FG1009-B2 | #1 CYCLONE B SEAL POT DOWN LEG PRESSURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | -1000~ 10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
25 | FE-FA1009-B1 | FE | FA1009-B1 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT A | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
26 | FE-FA1009-B2 | FE | FA1009-B2 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW ELEMENT B | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~5.5 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
36 | FG-FA1009-B1 | FG | FA1009-B1 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE A | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
37 | FG-FA1009-B2 | FG | FA1009-B2 | #1 CYCLONE B SEAL POT FLUIDIZING AIR SYSTEM FLOW GAUGE B | PD-054,3/3 | -330~8700 mmH2O | 150 | 0~4.5 | - | - | - | DIFF. PRESS. | FHI |  | 0 |  | FG
164 | TW-FG1009-B | TW | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
160 | TE-FG1009-B | TE | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE ELEMENT | PD-051 | -330~8700 mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
116 | TT-FG1009-B | TT | FG1009-B | #1 CYCLONE B SEAL POT TEMPERATURE TEMPERATURE TRANSMITTER | PD-051 | -330~8700 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
5 | FE-CD1122 | FE | CD1122 | #1 DEAERATOR IN CONDESATE FLOW ELEMENT | PD-016 | 24 | 200 | 0~450 | <2500 | - | - | FLOW NOZZLE | FHI |  | 0 |  | FE
5 | FT-CD1122 | FT | CD1122 | #1 DEAERATOR INLET CONDESATE FLOW TRANSMITTER | PD-016 | 24 | 200 | 0~450 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
21 | PT-CD1122 | PT | CD1122 | #1 DEAERATOR INLET CONDESATE PRESSURE TRANSMITTER | PD-016 | 24 | 200 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
76 | TW-CD1122 | TW | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
65 | TE-CD1122 | TE | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
48 | TT-CD1122 | TT | CD1122 | #1 DEAERATOR INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
40 | TW-TS1021 | TW | TS1021 | #1 DEAERATOR INLET STEAM TEMPERATURE GAUGE | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
4 | TG-TS1021 | TG | TS1021 | #1 DEAERATOR INLET STEAM TEMPERATURE GAUGE | PD-013 | 6.2 | 380 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
11 | LCV-CD1104 | LCV | CD1104 | #1 DEAERATOR LEVEL CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
41 | ZT-CD1104 | ZT | CD1104 | #1 DEAERATOR LEVEL CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
7 | FG-SP1005 | FG | SP1005 | #1 DEAERATOR OUTLET FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
6 | FG-SP1004 | FG | SP1004 | #1 DEAERATOR OUTLET FLOWMETER FOR DISSOLVED OXYGEN SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
5 | FG-SP1003 | FG | SP1003 | #1 DEAERATOR OUTLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
122 | PG-SP1002 | PG | SP1002 | #1 DEAERATOR OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
88 | TG-SP1002 | TG | SP1002 | #1 DEAERATOR OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
5 | AT-SP1005 | AT | SP1005 | #1 DEAERATOR OUTLET WATER CATION CONDUCTIVITY | PD-044 | 9 | 180 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
4 | AT-SP1004 | AT | SP1004 | #1 DEAERATOR OUTLET WATER DISSOLVED OXYGEN | PD-044 | 9 | 180 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
3 | AT-SP1003 | AT | SP1003 | #1 DEAERATOR OUTLET WATER PH | PD-044 | 9 | 180 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
7 | PCV-AS1030 | PCV | AS1030 | #1 DEAERATOR PEGGING STEAM CONTROL VALVE | PD-014 | 13 | 410 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
28 | ZT-AS1030 | ZT | AS1030 | #1 DEAERATOR PEGGING STEAM CONTROL VALVE POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
17 | PG-CD1104 | PG | CD1104 | #1 DEAERATOR PRESSURE GAUGE | PD-016 | 8 | 380 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
18 | PT-CD1104 | PT | CD1104 | #1 DEAERATOR PRESSURE TRANSMITTER | PD-016 | 8 | 380 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
63 | TW-CD1104-2 | TW | CD1104-2 | #1 DEAERATOR STORAGE TANK TEMPERATURE GAUGE | PD-016 | 8 | 170 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
14 | TG-CD1104-2 | TG | CD1104-2 | #1 DEAERATOR STORAGE TANK TEMPERATURE GAUGE | PD-016 | 8 | 170 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
1 | LG-CD1104 | LG | CD1104 | #1 DEAERATOR STORAGE TANK WATER LEVEL GAUGE | PD-016 | 8 | 170 | 0~2550 | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
3 | LSLL-CD1104-4 | LSLL | CD1104-4 | #1 DEAERATOR STORAGE TANK WATER LEVEL LOW-LOW SWITCH-4 | PD-016 | 8 | 170 | - | DI | FIELD | ARP | FLOAT | FHI |  | 0 |  | LS
1 | LT-CD1104-1 | LT | CD1104-1 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-1 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
2 | LT-CD1104-2 | LT | CD1104-2 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-2 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
3 | LT-CD1104-3 | LT | CD1104-3 | #1 DEAERATOR STORAGE TANK WATER LEVEL TRANSMITTER-3 | PD-016 | 8 | 170 | 0~3400 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
61 | TW-CD1104 | TW | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE ELEMENT | PD-016 | 8 | 170 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
39 | TE-CD1104 | TE | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE ELEMENT | PD-016 | 8 | 170 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
28 | TT-CD1104 | TT | CD1104 | #1 DEAERATOR STORAGE TANK WATER TEMPERATURE TRANSMITTER | PD-016 | 8 | 170 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
62 | TW-CD1104-1 | TW | CD1104-1 | #1 DEAERATOR TEMPERATURE GAUGE | PD-016 | 8 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
13 | TG-CD1104-1 | TG | CD1104-1 | #1 DEAERATOR TEMPERATURE GAUGE | PD-016 | 8 | 380 | 0~400 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
4 | FG-SP1002 | FG | SP1002 | #1 DEAERATOR UPSTREAM FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
3 | FG-SP1001 | FG | SP1001 | #1 DEAERATOR UPSTREAM FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
121 | PG-SP1001 | PG | SP1001 | #1 DEAERATOR UPSTREAM PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
87 | TG-SP1001 | TG | SP1001 | #1 DEAERATOR UPSTREAM THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
2 | AT-SP1002 | AT | SP1002 | #1 DEAERATOR UPSTREAM WATER CATION CONDUCTIVITY | PD-044 | 24 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
1 | AT-SP1001 | AT | SP1001 | #1 DEAERATOR UPSTREAM WATER PH | PD-044 | 24 | 65 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
7 | DPT-SW1502 | DPT | SW1502 | #1 DEBRIS FILTER S-1502 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~2000 mmH2O | AI 4~20mA | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | DPT
41 | MV-SW1001 | MV | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV | PD-020 | 5 | 50 | - | DO | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | MV
183 | ZSC-SW1001 | ZSC | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
184 | ZSO-SW1001 | ZSO | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
185 | TS-SW1001 | TS | SW1001 | #1 DEBRIS FILTER S-1502 DRAIN MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
8 | DPT-SW1504 | DPT | SW1504 | #1 DEBRIS FILTER S-1504 DIFFERENTIAL PRESSURE TRANSMITTER | PD-020 | - | 50 | 0~2000 mmH2O | AI 4~20mA | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | DPT
42 | MV-SW1002 | MV | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV | PD-020 | 7 | 50 | - | DO | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) |  | 0 |  | MV
186 | ZSC-SW1002 | ZSC | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV CLOSE POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
187 | ZSO-SW1002 | ZSO | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV OPEN POSITION SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
188 | TS-SW1002 | TS | SW1002 | #1 DEBRIS FILTER S-1504 DRAIN MOV TORQUE SWITCH | PD-020 | - | - | - | DI | FIELD | LCP | - | PACKAGE (DEBRIS FILTER) | NEW ADDED | 0 |  | ZS
38 | PCV-DO1009 | PCV | DO1009 | #1 DIESEL OIL RETURN PRESSURE CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
77 | ZT-DO1009 | ZT | DO1009 | #1 DIESEL OIL RETURN PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
85 | PG-DO1007 | PG | DO1007 | #1 DIESEL OIL RETURN PRESSURE GAUGE | PD-022,1/5 | 25 | 70 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
38 | PT-DO1008 | PT | DO1008 | #1 DIESEL OIL RETURN PRESSURE TRANSMITTER | PD-022,1/5 | 25 | 70 | 0~25 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | PT
78 | ZT-DO1012 | ZT | DO1012 | #1 DIESEL OIL SUPPLY TO BURNER #1 FLOW CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
36 | FCV-DO1012 | FCV | DO1012 | #1 DIESEL OIL SUPPLY TO BURNER FLOW CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 1 |  | CV
160 | TW-DO1006 | TW | DO1006 | #1 DIESEL OIL TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
83 | TG-DO1006 | TG | DO1006 | #1 DIESEL OIL TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
12 | AT-SP1012 | AT | SP1012 | #1 DRUM WATER(BLOW DOWN) SPECIFIC CONDUCTIVITY | PD-044 | 148 | 343 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
15 | LT-BR1001-1 | LT | BR1001-1 | #1 DRUM LEVEL -1 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
16 | LT-BR1001-2 | LT | BR1001-2 | #1 DRUM LEVEL -2 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
17 | LT-BR1001-3 | LT | BR1001-3 | #1 DRUM LEVEL -3 TRANSMITTER | PD-019 | 153.5 | 343 | -1270~0 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | LT
11 | LG-BR1001-1 | LG | BR1001-1 | #1 DRUM LEVEL GAUGE | PD-019 | 155.4 | 343 | 0~470 | - | - | - | BI-COLOR | FHI |  | 0 |  | LG
12 | LG-BR1001-2 | LG | BR1001-2 | #1 DRUM LEVEL GAUGE | PD-019 | 155.4 | 343 | 0~470 | - | - | - | BI-COLOR | FHI |  | 0 |  | LG
16 | LSHH-BR1001-1 | LSHH | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (HIGH HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
15 | LSH-BR1001-1 | LSH | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
18 | LSLL-BR1001-1 | LSLL | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
17 | LSL-BR1001-1 | LSL | BR1001-1 | #1 DRUM LEVEL SWITCH-1 (LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
19 | LSLL-BR1001-1-NC | LSLL | BR1001-1-NC | #1 DRUM LEVEL SWITCH-1 (NOT LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
24 | LSLL-BR1001-2-NC | LSLL | BR1001-2-NC | #1 DRUM LEVEL SWITCH-2 ( NOT LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
21 | LSHH-BR1001-2 | LSHH | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (HIGH HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
20 | LSH-BR1001-2 | LSH | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (HIGH) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
23 | LSLL-BR1001-2 | LSLL | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (LOW LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | IRP | ELECTRODE | FHI |  | 0 |  | LS
22 | LSL-BR1001-2 | LSL | BR1001-2 | #1 DRUM LEVEL SWITCH-2 (LOW) | PD-019 | 155.4 | 343 | - | DI | FIELD | DCS | ELECTRODE | FHI |  | 0 |  | LS
54 | PG-BR1001 | PG | BR1001 | #1 DRUM PRESSURE GAUGE | PD-019 | 155 | 343 | 0~200 | - | - | - | BOURDON | FHI |  | 0 |  | PG
26 | PT-BR1001-1 | PT | BR1001-1 | #1 DRUM PRESSURE TRANSMITTER-1 | PD-019 | 155 | 343 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
27 | PT-BR1001-2 | PT | BR1001-2 | #1 DRUM PRESSURE TRANSMITTER-2 | PD-019 | 155 | 343 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
14 | FG-SP1012 | FG | SP1012 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
13 | FG-SP1011 | FG | SP1011 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
15 | FG-SP1013 | FG | SP1013 | #1 DRUM WATER (BLOW DOWN) FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
91 | TG-SP1005 | TG | SP1005 | #1 DRUM WATER (BLOW DOWN) PRESSUE GAUGE | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
125 | PG-SP1005 | PG | SP1005 | #1 DRUM WATER (BLOW DOWN) PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
11 | AT-SP1011 | AT | SP1011 | #1 DRUM WATER(BLOW DOWN) PH | PD-044 | 148 | 343 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
13 | AT-SP1013 | AT | SP1013 | #1 DRUM WATER(BLOW DOWN)SILICA | PD-044 | 148 | 343 | 0~500ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
201 | TW-FG1111 | TW | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 450 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
197 | TE-FG1111 | TE | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 450 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
160 | TT-FG1111 | TT | FG1111 | #1 ECONOMIZER # 2S INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 450 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
202 | TW-FG1113 | TW | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE ELEMENT-B | PD-051 | ±890mmH2O | 430 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
198 | TE-FG1113 | TE | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE ELEMENT-B | PD-051 | ±890mmH2O | 430 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
161 | TT-FG1113 | TT | FG1113 | #1 ECONOMIZER # 2S OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 430 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
199 | TW-FG1109 | TW | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
195 | TE-FG1109 | TE | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
158 | TT-FG1109 | TT | FG1109 | #1 ECONOMIZER # 3 LOWER INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 520 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
197 | TW-FG1107 | TW | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 590 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
193 | TE-FG1107 | TE | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 590 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
156 | TT-FG1107 | TT | FG1107 | #1 ECONOMIZER # 3 UPPER INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 590 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
83 | TW-FW1011 | TW | FW1011 | #1 BFP COMMON DISCHARGE WATER TEMPERATURE ELEMENT | PD-017 | 230 | 180 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
84 | TW-FW1105 | TW | FW1105 | #1 HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 220 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
85 | TW-FW1106 | TW | FW1106 | #1 HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-017 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
116 | TW-FW1160 | TW | FW1160 | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
117 | TW-FW1160(G) | TW | FW1160(G) | #1 ECONOMIZER #1 ASSAMBLY INLET FEEDWATER TEMPERATURE GAUGE | PD-019 | 230 | 275 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
86 | TW-FW1601 | TW | FW1601 | #1 TEST WELL AT BFP INLET | PD-017 | 10 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
12 | FG-SP1010 | FG | SP1010 | #1 ECONOMIZER INLET FLOWMETER FOR DISSOLVED OXYGEN SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
11 | FG-SP1009 | FG | SP1009 | #1 ECONOMIZER INLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
124 | PG-SP1004 | PG | SP1004 | #1 ECONOMIZER INLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
90 | TG-SP1004 | TG | SP1004 | #1 ECONOMIZER INLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
10 | AT-SP1010 | AT | SP1010 | #1 ECONOMIZER INLET WATER DISSOLVED OXYGEN | PD-044 | 215 | 275 | 0~20ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
9 | AT-SP1009 | AT | SP1009 | #1 ECONOMIZER INLET WATER PH | PD-044 | 215 | 275 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
198 | TW-FG1108 | TW | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 480 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
194 | TE-FG1108 | TE | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 480 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
157 | TT-FG1108 | TT | FG1108 | #1 ECONOMIZER NO. 2R INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 480 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
200 | TW-FG1110 | TW | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE ELEMENT-A | PD-051 | ±890mmH2O | 430 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
196 | TE-FG1110 | TE | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE ELEMENT-A | PD-051 | ±890mmH2O | 430 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
159 | TT-FG1110 | TT | FG1110 | #1 ECONOMIZER NO. 2R OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 430 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
104 | TW-BR1020 | TW | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
94 | TE-BR1020 | TE | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
71 | TT-BR1020 | TT | BR1020 | #1 ECONOMIZER NO.1 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
105 | TW-BR1030 | TW | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
95 | TE-BR1030 | TE | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
72 | TT-BR1030 | TT | BR1030 | #1 ECONOMIZER NO.2 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
106 | TW-BR1040 | TW | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
96 | TE-BR1040 | TE | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE ELEMENT | PD-019 | 157 | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
73 | TT-BR1040 | TT | BR1040 | #1 ECONOMIZER NO.3 OUTLET FEEDWATER TEMPERATURE TRANSMITTER | PD-019 | 157 | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
28 | AT-FG1122 | AT | FG1122 | #1 ECONOMIZER OUTLET FLUE GAS O2 (A) | PD-051 | ±890mmAq | 371 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0 |  | AT
29 | AT-FG1123 | AT | FG1123 | #1 ECONOMIZER OUTLET FLUE GAS O2 (B) | PD-051 | ±890mmAq | 371 | 0~21% | WET AI 4~20mA | FIELD | DCS | ZIRCONIA | PACKAGE (CEMS) |  | 0 |  | AT
37 | TW-TS1014 | TW | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE ELEMENT | PD-013 | 16 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
26 | TE-TS1014 | TE | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE ELEMENT | PD-013 | 16 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
21 | MV-TS1400 | MV | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV | PD-013 | 1.5 | 120 | - | DO | DCS | FIELD |  | FHI | NEW ADDED | 0 |  | MV
79 | ZSC-TS1400 | ZSC | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZS
80 | ZSO-TS1400 | ZSO | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZS
24 | ZT-TS1400 | ZT | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZT
81 | TS-TS1400 | TS | TS1400 | #1 EXTRACTION STEAM #3 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI | NEW ADDED | 0 |  | ZS
70 | ZSC-TS1397 | ZSC | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
52 | ZSC-TS1391 | ZSC | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
71 | ZSO-TS1397 | ZSO | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
53 | ZSO-TS1391 | ZSO | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
21 | ZT-TS1397 | ZT | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
15 | ZT-TS1391 | ZT | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
72 | TS-TS1397 | TS | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
54 | TS-TS1391 | TS | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
18 | MV-TS1397 | MV | TS1397 | #1 EXTRACTION STEAM NO.1 DRAIN MOV(HEATER SIDE) | PD-013 | 45 | 395 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
12 | MV-TS1391 | MV | TS1391 | #1 EXTRACTION STEAM NO.1 DRAIN MOV(TURBINE SIDE) | PD-013 | 45 | 395 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
5 | MV-TS1001 | MV | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV | PD-013 | 45 | 395 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
31 | ZSC-TS1001 | ZSC | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
32 | ZSO-TS1001 | ZSO | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
8 | ZT-TS1001 | ZT | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
33 | TS-TS1001 | TS | TS1001 | #1 EXTRACTION STEAM NO.1 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
67 | ZSC-TS1396 | ZSC | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
55 | ZSC-TS1392 | ZSC | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
68 | ZSO-TS1396 | ZSO | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
56 | ZSO-TS1392 | ZSO | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
20 | ZT-TS1396 | ZT | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
16 | ZT-TS1392 | ZT | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
69 | TS-TS1396 | TS | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
57 | TS-TS1392 | TS | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
17 | MV-TS1396 | MV | TS1396 | #1 EXTRACTION STEAM NO.2 DRAIN MOV(HEATER SIDE) | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
13 | MV-TS1392 | MV | TS1392 | #1 EXTRACTION STEAM NO.2 DRAIN MOV(TURBINE SIDE) | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
11 | PT-TS1013 | PT | TS1013 | #1 EXTRACTION STEAM NO.2 PRESSURE TRANSMITTER | PD-013 | 16 | 440 | 0~25 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
6 | MV-TS1002 | MV | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV | PD-013 | 16 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
34 | ZSC-TS1002 | ZSC | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
35 | ZSO-TS1002 | ZSO | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
9 | ZT-TS1002 | ZT | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
36 | TS-TS1002 | TS | TS1002 | #1 EXTRACTION STEAM NO.2 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
38 | TW-TS1016 | TW | TS1016 | #1 EXTRACTION STEAM NO.2 TEMPERATURE GAUGE | PD-013 | 16 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
3 | TG-TS1016 | TG | TS1016 | #1 EXTRACTION STEAM NO.2 TEMPERATURE GAUGE | PD-013 | 16 | 440 | 0~600 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
15 | TT-TS1014 | TT | TS1014 | #1 EXTRACTION STEAM NO.2 TEMPERATURE TRANSMITTER | PD-013 | 16 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
20 | MV-TS1399 | MV | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
76 | ZSC-TS1399 | ZSC | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
73 | ZSC-TS1398 | ZSC | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
58 | ZSC-TS1393 | ZSC | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
77 | ZSO-TS1399 | ZSO | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
74 | ZSO-TS1398 | ZSO | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
59 | ZSO-TS1393 | ZSO | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
23 | ZT-TS1399 | ZT | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
22 | ZT-TS1398 | ZT | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER(DEAERATORR SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
17 | ZT-TS1393 | ZT | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
78 | TS-TS1399 | TS | TS1399 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
75 | TS-TS1398 | TS | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH(DEAERATORR SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
60 | TS-TS1393 | TS | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
19 | MV-TS1398 | MV | TS1398 | #1 EXTRACTION STEAM NO.3 DRAIN MOV(DEAERATORR SIDE) | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
14 | MV-TS1393 | MV | TS1393 | #1 EXTRACTION STEAM NO.3 DRAIN MOV(TURBINE SIDE) | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
12 | PT-TS1017 | PT | TS1017 | #1 EXTRACTION STEAM NO.3 PRESSURE TRANSMITTER | PD-013 | 6.2 | 380 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
7 | MV-TS1003 | MV | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV | PD-013 | 6.2 | 380 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
37 | ZSC-TS1003 | ZSC | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
38 | ZSO-TS1003 | ZSO | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
10 | ZT-TS1003 | ZT | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
39 | TS-TS1003 | TS | TS1003 | #1 EXTRACTION STEAM NO.3 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
39 | TW-TS1018 | TW | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE ELEMENT | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
27 | TE-TS1018 | TE | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE ELEMENT | PD-013 | 6.2 | 380 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
16 | TT-TS1018 | TT | TS1018 | #1 EXTRACTION STEAM NO.3 STEAM TEMPERATURE TRANSMITTER | PD-013 | 6.2 | 380 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
49 | ZSC-TS1390 | ZSC | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
61 | ZSC-TS1394 | ZSC | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
50 | ZSO-TS1390 | ZSO | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
62 | ZSO-TS1394 | ZSO | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
14 | ZT-TS1390 | ZT | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
18 | ZT-TS1394 | ZT | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
51 | TS-TS1390 | TS | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
63 | TS-TS1394 | TS | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
11 | MV-TS1390 | MV | TS1390 | #1 EXTRACTION STEAM NO.4 DRAIN MOV(HEATER SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
15 | MV-TS1394 | MV | TS1394 | #1 EXTRACTION STEAM NO.4 DRAIN MOV(TURBINE SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
13 | PT-TS1022 | PT | TS1022 | #1 EXTRACTION STEAM NO.4 PRESSURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
8 | MV-TS1004 | MV | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
40 | ZSC-TS1004 | ZSC | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
42 | ZSC-TS1004 | ZSC | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV CLOSE POSITION TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
41 | ZSO-TS1004 | ZSO | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
11 | ZT-TS1004 | ZT | TS1004 | #1 EXTRACTION STEAM NO.4 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
41 | TW-TS1023 | TW | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
28 | TE-TS1023 | TE | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
42 | TW-TS1025 | TW | TS1025 | #1 EXTRACTION STEAM NO.4 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
5 | TG-TS1025 | TG | TS1025 | #1 EXTRACTION STEAM NO.4 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
17 | TT-TS1023 | TT | TS1023 | #1 EXTRACTION STEAM NO.4 TEMPERATURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
46 | ZSC-TS1389 | ZSC | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV CLOSE POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
64 | ZSC-TS1395 | ZSC | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV CLOSE POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
47 | ZSO-TS1389 | ZSO | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV OPEN POSITION SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
65 | ZSO-TS1395 | ZSO | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV OPEN POSITION SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
13 | ZT-TS1389 | ZT | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV POSITION TRANSMITTER(HEATER SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
19 | ZT-TS1395 | ZT | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV POSITION TRANSMITTER(TURBINE SIDE) | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
48 | TS-TS1389 | TS | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV TORQUE SWITCH(HEATER SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
66 | TS-TS1395 | TS | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV TORQUE SWITCH(TURBINE SIDE) | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
10 | MV-TS1389 | MV | TS1389 | #1 EXTRACTION STEAM NO.5 DRAIN MOV(HEATER SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD |  | FHI |  | 0 |  | MV
16 | MV-TS1395 | MV | TS1395 | #1 EXTRACTION STEAM NO.5 DRAIN MOV(TURBINE SIDE) | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
14 | PT-TS1026 | PT | TS1026 | #1 EXTRACTION STEAM NO.5 PRESSURE TRANSMITTER | PD-013 | 3.6 | 285 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
9 | MV-TS1005 | MV | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV | PD-013 | 3.6 | 285 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
43 | ZSC-TS1005 | ZSC | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV CLOSE POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
44 | ZSO-TS1005 | ZSO | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV OPEN POSITION SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
12 | ZT-TS1005 | ZT | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV POSITION TRANSMITTER | PD-013 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
45 | TS-TS1005 | TS | TS1005 | #1 EXTRACTION STEAM NO.5 SHUT-OFF MOV TORQUE SWITCH | PD-013 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
43 | TW-TS1027 | TW | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
29 | TE-TS1027 | TE | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE ELEMENT | PD-013 | 3.6 | 285 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
44 | TW-TS1029 | TW | TS1029 | #1 EXTRACTION STEAM NO.5 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
6 | TG-TS1029 | TG | TS1029 | #1 EXTRACTION STEAM NO.5 TEMPERATURE GAUGE | PD-013 | 3.6 | 285 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
18 | TT-TS1027 | TT | TS1027 | #1 EXTRACTION STEAM NO.5 TEMPERATURE TRANSMITTER | PD-013 | 3.6 | 285 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
81 | TT-BR1150-1 | TT | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
82 | TT-BR1150-2 | TT | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
29 | PT-BR1150 | PT | BR1150 | #1 FINAL SUPERHEATER INLET STEAM PRESSURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
114 | TW-BR1150-1 | TW | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
115 | TW-BR1150-2 | TW | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
104 | TE-BR1150-1 | TE | BR1150-1 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
105 | TE-BR1150-2 | TE | BR1150-2 | #1 FINAL SUPERHEATER INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
191 | TW-FG1101 | TW | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
187 | TE-FG1101 | TE | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
150 | TT-FG1101 | TT | FG1101 | #1 FINISHING SUPERHEATER-1 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 900 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
193 | TW-FG1103 | TW | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
189 | TE-FG1103 | TE | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
152 | TT-FG1103 | TT | FG1103 | #1 FINISHING SUPERHEATER-2 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 700 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
195 | TW-FG1105 | TW | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 620 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
191 | TE-FG1105 | TE | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 620 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
154 | TT-FG1105 | TT | FG1105 | #1 FINISHING SUPERHEATER-3 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 620 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
11 | XV-CD1005 | XV | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
117 | ZSC-CD1005 | ZSC | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
118 | ZSO-CD1005 | ZSO | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
13 | SV-CD1005 | SV | CD1005 | #1 FLASH CHAMBER SPRAY CONTROL VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
10 | XV-CD1004 | XV | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
115 | ZSC-CD1004 | ZSC | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
116 | ZSO-CD1004 | ZSO | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
12 | SV-CD1004 | SV | CD1004 | #1 FLASH CHAMBER SPRAY CONTROL VALVE(NORMAL OPERATION) SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
24 | XV-FS1005 | XV | FS1005 | #1 FLASH PIPE DRAIN VALVE | PD-027 | 8 | 280 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
209 | ZSC-FS1005 | ZSC | FS1005 | #1 FLASH PIPE DRAIN VALVE CLOSE POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
210 | ZSO-FS1005 | ZSO | FS1005 | #1 FLASH PIPE DRAIN VALVE OPEN POSITION SWITCH | PD-027 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
31 | SV-FS1005 | SV | FS1005 | #1 FLASH PIPE DRAIN VALVE SOLENOID VALVE | PD-027 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
30 | LS-FS1410 | LS | FS1410 | #1 FLASH PIPE LEVEL HIGH SWITCH | PD-027 | 3 | 410 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
31 | LS-FS1411 | LS | FS1411 | #1 FLASH PIPE LEVEL LOW SWITCH | PD-027 | 3 | 410 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
10 | LG-BD1050 | LG | BD1050 | #1 FLASH TANK LEVEL GAUGE | PD-019 | 12.5 | 193 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
53 | PG-BD1050 | PG | BD1050 | #1 FLASH TANK PRESSURE GAUGE | PD-019 | 12.5 | 200 | 0~15 | - | - | - | BOURDON | FHI |  | 0 |  | PG
39 | TCV-FG1116-A | TCV | FG1116-A | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-1 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
81 | ZT-FG1116-A | ZT | FG1116-A | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-1 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
40 | TCV-FG1116-B | TCV | FG1116-B | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-2 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
82 | ZT-FG1116-B | ZT | FG1116-B | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-2 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
41 | TCV-FG1116-C | TCV | FG1116-C | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-3 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
83 | ZT-FG1116-C | ZT | FG1116-C | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-3 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
42 | TCV-FG1116-D | TCV | FG1116-D | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-4 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
84 | ZT-FG1116-D | ZT | FG1116-D | #1 FLUE GAS BIASING DAMPER (REHEATER PASS)-4 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
43 | TCV-FG1117-A | TCV | FG1117-A | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-1 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
85 | ZT-FG1117-A | ZT | FG1117-A | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-1 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
44 | TCV-FG1117-B | TCV | FG1117-B | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-2 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
86 | ZT-FG1117-B | ZT | FG1117-B | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-2 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
45 | TCV-FG1117-C | TCV | FG1117-C | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-3 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
87 | ZT-FG1117-C | ZT | FG1117-C | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-3 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
46 | TCV-FG1117-D | TCV | FG1117-D | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-4 | PD-051 | 889 mmAq | 427 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
88 | ZT-FG1117-D | ZT | FG1117-D | #1 FLUE GAS BIASING DAMPER (SUPERHEATER PASS)-4 POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
197 | TT-FA1055-AV | TT | FA1055-AV | #1 FLUIDIZING AIR BLOWER (A )MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
193 | TT-FA1055-A2 | TT | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
3 | FCV-FA1055-A1 | FCV | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE | PD-054 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
47 | ZSC-FA1055-A1 | ZSC | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
53 | ZSO-FA1055-A1 | ZSO | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
59 | ZT-FA1055-A1 | ZT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) INLET VALVE POSITION TRANSMITTER | PD-054 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
44 | XV-FA1055-A3 | XV | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
49 | ZSC-FA1055-A3 | ZSC | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
55 | ZSO-FA1055-A3 | ZSO | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
12 | SV-FA1055-A3 | SV | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) ISOLATING VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
194 | TT-FA1055-A3 | TT | FA1055-A3 | #1 FLUIDIZING AIR BLOWER (A) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
195 | TT-FA1055-A4 | TT | FA1055-A4 | #1 FLUIDIZING AIR BLOWER (A) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
196 | TT-FA1055-AU | TT | FA1055-AU | #1 FLUIDIZING AIR BLOWER (A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
198 | TT-FA1055-AW | TT | FA1055-AW | #1 FLUIDIZING AIR BLOWER (A) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
133 | PG-FA1055-A | PG | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET PRESSURE GAUGE | PD-054,1/3 | 8700 mmH2O | 150 | 0~10000 mmH2O | - | - | - | DIAPHRAGM | FHI |  | 0 |  | PG
218 | TW-FA1055-A | TW | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
214 | TE-FA1055-A | TE | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
191 | TT-FA1055-A | TT | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLET TEMPERATURE TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 149 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
73 | PT-FA1055-A | PT | FA1055-A | #1 FLUIDIZING AIR BLOWER (A) OUTLETT PRESSURE TRANSMITTER | PD-054 | -330~8700 mmH2O | 149 | 0~10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
192 | TT-FA1055-A1 | TT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER (A) REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
43 | XV-FA1055-A2 | XV | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
48 | ZSC-FA1055-A2 | ZSC | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
54 | ZSO-FA1055-A2 | ZSO | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
11 | SV-FA1055-A2 | SV | FA1055-A2 | #1 FLUIDIZING AIR BLOWER (A) SURGE VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
205 | TT-FA1055-BV | TT | FA1055-BV | #1 FLUIDIZING AIR BLOWER (B )MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
201 | TT-FA1055-B2 | TT | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
4 | FCV-FA1055-B1 | FCV | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE | PD-054 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
50 | ZSC-FA1055-B1 | ZSC | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
56 | ZSO-FA1055-B1 | ZSO | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
60 | ZT-FA1055-B1 | ZT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) INLET VALVE POSITION TRANSMITTER | PD-054 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
46 | XV-FA1055-B3 | XV | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
52 | ZSC-FA1055-B3 | ZSC | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
58 | ZSO-FA1055-B3 | ZSO | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
14 | SV-FA1055-B3 | SV | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) ISOLATING VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
202 | TT-FA1055-B3 | TT | FA1055-B3 | #1 FLUIDIZING AIR BLOWER (B) MOTOR FRONT BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
203 | TT-FA1055-B4 | TT | FA1055-B4 | #1 FLUIDIZING AIR BLOWER (B) MOTOR REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
206 | TT-FA1055-BW | TT | FA1055-BW | #1 FLUIDIZING AIR BLOWER (B) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
204 | TT-FA1055-BU | TT | FA1055-BU | #1 FLUIDIZING AIR BLOWER (B) MOTOR WINRING (U) TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
134 | PG-FA1055-B | PG | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET PRESSURE GAUGE | PD-054,1/3 | 8700 mmH2O | 150 | 0~10000 mmH2O | - | - | - | DIAPHRAGM | FHI |  | 0 |  | PG
74 | PT-FA1055-B | PT | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET PRESSURE TRANSMITTER | PD-054 | -330~8700 mmH2O | 149 | 0~10000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
219 | TW-FA1055-B | TW | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
215 | TE-FA1055-B | TE | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE ELEMENT | PD-054-1/3 | -330~8700 mmH2O | 149 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
199 | TT-FA1055-B | TT | FA1055-B | #1 FLUIDIZING AIR BLOWER (B) OUTLET TEMPERATURE TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 149 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
200 | TT-FA1055-B1 | TT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER (B) REAR BEARING TEMPERATURE TRANSMITTER | PD-054,1/3 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
45 | XV-FA1055-B2 | XV | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE | PD-054 | - | - | - | DO | DCS | FIELD | ON/OFF | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
51 | ZSC-FA1055-B2 | ZSC | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE CLOSE POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
57 | ZSO-FA1055-B2 | ZSO | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE OPEN POSITION SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
13 | SV-FA1055-B2 | SV | FA1055-B2 | #1 FLUIDIZING AIR BLOWER (B) SURGE VALVE SOLENOID VALVE | PD-054 | - | - | - | - | - | - | DC24V | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
22 | FE-FA1055 | FE | FA1055 | #1 FLUIDIZING AIR BLOWER OUTLET COMMON FLOW ELEMENT | PD-054,1/3 | -340~2500 mmH2O | 150 | 0~35 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
24 | FT-FA1055 | FT | FA1055 | #1 FLUIDIZING AIR BLOWER OUTLET COMMON FLOW TRANSMITTER | PD-054,1/3 | -330~8700 mmH2O | 150 | 0~35 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
16 | TE-FA1055-A2 | TE | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
36 | VT-FA1055-A2 | VT | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
1 | DPSH-FA1055-A | DPSH | FA1055-A | #1 FLUIDIZING AIR BLOWER(A) INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
17 | TE-FA1055-A3 | TE | FA1055-A3 | #1 FLUIDIZING AIR BLOWER(A) MOTOR FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
37 | VT-FA1055-A3 | VT | FA1055-A3 | #1 FLUIDIZING AIR BLOWER(A) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
18 | TE-FA1055-A4 | TE | FA1055-A4 | #1 FLUIDIZING AIR BLOWER(A) MOTOR REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
38 | VT-FA1055-A4 | VT | FA1055-A4 | #1 FLUIDIZING AIR BLOWER(A) MOTOR REAR BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
5 | LG-FA1055-A1 | LG | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) OIL LEVEL GAUGE(OIL CUP)-1 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
6 | LG-FA1055-A2 | LG | FA1055-A2 | #1 FLUIDIZING AIR BLOWER(A) OIL LEVEL GAUGE(OIL CUP)-2 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
9 | PG-FA1055-A | PG | FA1055-A | #1 FLUIDIZING AIR BLOWER(A) PRESSURE GAUGE | PD-054 | - | - | 0~1Kg/c㎡G | - | - | - | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
15 | TE-FA1055-A1 | TE | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
35 | VT-FA1055-A1 | VT | FA1055-A1 | #1 FLUIDIZING AIR BLOWER(A) REAR BEARING VIBRATION TRANSMITTER-1 | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
19 | TE-FA1055-AU1 | TE | FA1055-AU1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-U1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
20 | TE-FA1055-AU2 | TE | FA1055-AU2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-U2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
21 | TE-FA1055-AV1 | TE | FA1055-AV1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-V1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
22 | TE-FA1055-AV2 | TE | FA1055-AV2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE ELEMENT-V2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
23 | TE-FA1055-AW1 | TE | FA1055-AW1 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE -W1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
24 | TE-FA1055-AW2 | TE | FA1055-AW2 | #1 FLUIDIZING AIR BLOWER(A) WINDING TEMPERATUTRE -W2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
26 | TE-FA1055-B2 | TE | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
40 | VT-FA1055-B2 | VT | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
2 | DPSH-FA1055-B | DPSH | FA1055-B | #1 FLUIDIZING AIR BLOWER(B) INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-054 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
27 | TE-FA1055-B3 | TE | FA1055-B3 | #1 FLUIDIZING AIR BLOWER(B) MOTOR FRONT BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
41 | VT-FA1055-B3 | VT | FA1055-B3 | #1 FLUIDIZING AIR BLOWER(B) MOTOR FRONT BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
42 | VT-FA1055-B4 | VT | FA1055-B4 | #1 FLUIDIZING AIR BLOWER(B) MOTOR RAER BEARING VIBRATION TRANSMITTER | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
28 | TE-FA1055-B4 | TE | FA1055-B4 | #1 FLUIDIZING AIR BLOWER(B) MOTOR REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
7 | LG-FA1055-B1 | LG | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) OIL LEVEL GAUGE(OIL CUP)-1 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
8 | LG-FA1055-B2 | LG | FA1055-B2 | #1 FLUIDIZING AIR BLOWER(B) OIL LEVEL GAUGE(OIL CUP)-2 | PD-054 | - | - | - | - | - | - | - | PACKAGE (BLOWER) |  | 1 |  | FLUIDIZING AIR
10 | PG-FA1055-B | PG | FA1055-B | #1 FLUIDIZING AIR BLOWER(B) PRESSURE GAUGE | PD-054 | - | - | 0~1Kg/c㎡G | - | - | - | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
25 | TE-FA1055-B1 | TE | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) REAR BEARING TEMPERATUTRE ELEMENT | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
39 | VT-FA1055-B1 | VT | FA1055-B1 | #1 FLUIDIZING AIR BLOWER(B) REAR BEARING VIBRATION TRANSMITTER-1 | PD-054 | - | - | 0~10mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
29 | TE-FA1055-BU1 | TE | FA1055-BU1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-U1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
30 | TE-FA1055-BU2 | TE | FA1055-BU2 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-U2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
31 | TE-FA1055-BV1 | TE | FA1055-BV1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-V1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
32 | TE-FA1055-BV1 | TE | FA1055-BV1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-V2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
33 | TE-FA1055-BW1 | TE | FA1055-BW1 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-W1 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
34 | TE-FA1055-BW2 | TE | FA1055-BW2 | #1 FLUIDIZING AIR BLOWER(B) WINDING TEMPERATUTRE ELEMENT-W2 | PD-054 | - | - | - | - | FIELD | TT | - | PACKAGE (BLOWER) |  | 0 |  | FLUIDIZING AIR
125 | TT-FG1090-A | TT | FG1090-A | #1 FURNACE FRONT TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
134 | TT-FG1091-A | TT | FG1091-A | #1 FURNACE FRONT TEMPERATURE (A) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
126 | TT-FG1090-B | TT | FG1090-B | #1 FURNACE FRONT TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
135 | TT-FG1091-B | TT | FG1091-B | #1 FURNACE FRONT TEMPERATURE (B) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
127 | TT-FG1090-C | TT | FG1090-C | #1 FURNACE FRONT TEMPERATURE (C) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
136 | TT-FG1091-C | TT | FG1091-C | #1 FURNACE FRONT TEMPERATURE (C) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
128 | TT-FG1090-D | TT | FG1090-D | #1 FURNACE FRONT TEMPERATURE (D) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
137 | TT-FG1091-D | TT | FG1091-D | #1 FURNACE FRONT TEMPERATURE (D) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
129 | TT-FG1090-E | TT | FG1090-E | #1 FURNACE FRONT TEMPERATURE (E) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
138 | TT-FG1091-E | TT | FG1091-E | #1 FURNACE FRONT TEMPERATURE (E) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
130 | TT-FG1090-F | TT | FG1090-F | #1 FURNACE FRONT TEMPERATURE (F) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
139 | TT-FG1091-F | TT | FG1091-F | #1 FURNACE FRONT TEMPERATURE (F) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
166 | TW-FG1090-A | TW | FG1090-A | #1 FURNACE FRONT TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
162 | TE-FG1090-A | TE | FG1090-A | #1 FURNACE FRONT TEMPERATURE ELEMENT (A) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
167 | TW-FG1090-B | TW | FG1090-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
176 | TW-FG1091-B | TW | FG1091-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
163 | TE-FG1090-B | TE | FG1090-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
172 | TE-FG1091-B | TE | FG1091-B | #1 FURNACE FRONT TEMPERATURE ELEMENT (B) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
168 | TW-FG1090-C | TW | FG1090-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
177 | TW-FG1091-C | TW | FG1091-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
164 | TE-FG1090-C | TE | FG1090-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
173 | TE-FG1091-C | TE | FG1091-C | #1 FURNACE FRONT TEMPERATURE ELEMENT (C) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
169 | TW-FG1090-D | TW | FG1090-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
178 | TW-FG1091-D | TW | FG1091-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
165 | TE-FG1090-D | TE | FG1090-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
174 | TE-FG1091-D | TE | FG1091-D | #1 FURNACE FRONT TEMPERATURE ELEMENT (D) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
170 | TW-FG1090-E | TW | FG1090-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
179 | TW-FG1091-E | TW | FG1091-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
166 | TE-FG1090-E | TE | FG1090-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
175 | TE-FG1091-E | TE | FG1091-E | #1 FURNACE FRONT TEMPERATURE ELEMENT (E) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
171 | TW-FG1090-F | TW | FG1090-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
180 | TW-FG1091-F | TW | FG1091-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
167 | TE-FG1090-F | TE | FG1090-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
176 | TE-FG1091-F | TE | FG1091-F | #1 FURNACE FRONT TEMPERATURE ELEMENT (F) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
175 | TW-FG1091-A | TW | FG1091-A | #1 FURNACE FRONT TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
171 | TE-FG1091-A | TE | FG1091-A | #1 FURNACE FRONT TEMPERATURE ELEMENT(A) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
1 | MCV-FA1005 | MCV | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
61 | ZSC-FA1005 | ZSC | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
84 | ZSO-FA1005 | ZSO | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
107 | ZT-FA1005 | ZT | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
34 | TS-FA1005 | TS | FA1005 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.1 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
10 | MCV-FA1014 | MCV | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
70 | ZSC-FA1014 | ZSC | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
93 | ZSO-FA1014 | ZSO | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
116 | ZT-FA1014 | ZT | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
43 | TS-FA1014 | TS | FA1014 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.10 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
11 | MCV-FA1015 | MCV | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
71 | ZSC-FA1015 | ZSC | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
94 | ZSO-FA1015 | ZSO | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
117 | ZT-FA1015 | ZT | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
44 | TS-FA1015 | TS | FA1015 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.11 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
12 | MCV-FA1016 | MCV | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
72 | ZSC-FA1016 | ZSC | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
95 | ZSO-FA1016 | ZSO | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
118 | ZT-FA1016 | ZT | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
45 | TS-FA1016 | TS | FA1016 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.12 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
13 | MCV-FA1017 | MCV | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
73 | ZSC-FA1017 | ZSC | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
96 | ZSO-FA1017 | ZSO | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
119 | ZT-FA1017 | ZT | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
46 | TS-FA1017 | TS | FA1017 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.13 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
14 | MCV-FA1018 | MCV | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
74 | ZSC-FA1018 | ZSC | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
97 | ZSO-FA1018 | ZSO | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
120 | ZT-FA1018 | ZT | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
47 | TS-FA1018 | TS | FA1018 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.14 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
2 | MCV-FA1006 | MCV | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
62 | ZSC-FA1006 | ZSC | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
85 | ZSO-FA1006 | ZSO | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
108 | ZT-FA1006 | ZT | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
35 | TS-FA1006 | TS | FA1006 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.2 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
3 | MCV-FA1007 | MCV | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
63 | ZSC-FA1007 | ZSC | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
86 | ZSO-FA1007 | ZSO | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
109 | ZT-FA1007 | ZT | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
36 | TS-FA1007 | TS | FA1007 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.3 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
4 | MCV-FA1008 | MCV | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
64 | ZSC-FA1008 | ZSC | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
87 | ZSO-FA1008 | ZSO | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
110 | ZT-FA1008 | ZT | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
37 | TS-FA1008 | TS | FA1008 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.4 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
5 | MCV-FA1009 | MCV | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
65 | ZSC-FA1009 | ZSC | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
88 | ZSO-FA1009 | ZSO | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
111 | ZT-FA1009 | ZT | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
38 | TS-FA1009 | TS | FA1009 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.5 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
6 | MCV-FA1010 | MCV | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
66 | ZSC-FA1010 | ZSC | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
89 | ZSO-FA1010 | ZSO | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
112 | ZT-FA1010 | ZT | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
39 | TS-FA1010 | TS | FA1010 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.6 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
7 | MCV-FA1011 | MCV | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
67 | ZSC-FA1011 | ZSC | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
90 | ZSO-FA1011 | ZSO | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
113 | ZT-FA1011 | ZT | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
40 | TS-FA1011 | TS | FA1011 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.7 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
8 | MCV-FA1012 | MCV | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
68 | ZSC-FA1012 | ZSC | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
91 | ZSO-FA1012 | ZSO | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
114 | ZT-FA1012 | ZT | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
41 | TS-FA1012 | TS | FA1012 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.8 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
9 | MCV-FA1013 | MCV | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
69 | ZSC-FA1013 | ZSC | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
92 | ZSO-FA1013 | ZSO | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
115 | ZT-FA1013 | ZT | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
42 | TS-FA1013 | TS | FA1013 | #1 FURNACE FRONT WALL CONTROL DAMPER MOV NO.9 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
21 | DPT-FG1084 | DPT | FG1084 | #1 FURNACE GRATE DIFFERENTIAL PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
23 | DPT-FG1184 | DPT | FG1184 | #1 FURNACE GRATE DIFFERENTIAL PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI | NEW ADDED | 0 |  | DPT
24 | FG-1401 | FG | 1401 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
25 | FG-1402 | FG | 1402 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
26 | FG-1404 | FG | 1404 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
27 | FG-1405 | FG | 1405 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
28 | FG-1406 | FG | 1406 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
29 | FG-1407 | FG | 1407 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
30 | FG-1408 | FG | 1408 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
31 | FG-1409 | FG | 1409 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
32 | FG-1420 | FG | 1420 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
33 | FG-1422 | FG | 1422 | #1 FURNACE PLENUM SAMPLING POINT PURGE AIR FLOWMETER (PURGE SET) | PD-051 | 10 | 50 | 60~300CC/min | - | - | - | ROTEMETER | FHI | NEW ADDED | 0 |  | FG
14 | PSHH-FG1085 | PSHH | FG1085 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
16 | PSHH-FG1086 | PSHH | FG1086 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
18 | PSHH-FG1087 | PSHH | FG1087 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
20 | PSHHH-FG1085 | PSHHH | FG1085 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
22 | PSHHH-FG1086 | PSHHH | FG1086 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
24 | PSHHH-FG1087 | PSHHH | FG1087 | #1 FURNACE PRESSURE SWITCH HIGH-HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
26 | PSLL-FG1085 | PSLL | FG1085 | #1 FURNACE PRESSURE SWITCH LOW-LOW (A) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
28 | PSLL-FG1086 | PSLL | FG1086 | #1 FURNACE PRESSURE SWITCH LOW-LOW (B) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
30 | PSLL-FG1087 | PSLL | FG1087 | #1 FURNACE PRESSURE SWITCH LOW-LOW (C) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
15 | PSHH-FG1085-NC | PSHH | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
17 | PSHH-FG1086-NC | PSHH | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
19 | PSHH-FG1087-NC | PSHH | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
21 | PSHHH-FG1085-NC | PSHHH | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (A) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
23 | PSHHH-FG1086-NC | PSHHH | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (B) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
25 | PSHHH-FG1087-NC | PSHHH | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT HIGH-HIGH-HIGH (C) | PD-051 | ±890 mmH2O | 1200 | 381 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
27 | PSLL-FG1085-NC | PSLL | FG1085-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (A) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
29 | PSLL-FG1086-NC | PSLL | FG1086-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (B) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
31 | PSLL-FG1087-NC | PSLL | FG1087-NC | #1 FURNACE PRESSURE SWITCH NOT LOW-LOW (C) | PD-051 | ±890 mmH2O | 1200 | -267 mmH2O | DI | FIELD | IRP | DIAPHRAGM | FHI |  | 0 |  | PS
60 | PT-FG1085 | PT | FG1085 | #1 FURNACE PRESSURE TRANSMITTER (A) | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
61 | PT-FG1086 | PT | FG1086 | #1 FURNACE PRESSURE TRANSMITTER (B) | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
62 | PT-FG1087-1 | PT | FG1087-1 | #1 FURNACE PRESSURE TRANSMITTER (C) -1 | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
63 | PT-FG1087-2 | PT | FG1087-2 | #1 FURNACE PRESSURE TRANSMITTER (C) -2 | PD-051 | ±890 mmH2O | 1200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
131 | TT-FG1090-G | TT | FG1090-G | #1 FURNACE REAR TEMPERATURE (G) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
140 | TT-FG1091-G | TT | FG1091-G | #1 FURNACE REAR TEMPERATURE (G) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
132 | TT-FG1090-H | TT | FG1090-H | #1 FURNACE REAR TEMPERATURE (H) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
141 | TT-FG1091-H | TT | FG1091-H | #1 FURNACE REAR TEMPERATURE (H) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
133 | TT-FG1090-I | TT | FG1090-I | #1 FURNACE REAR TEMPERATURE (I) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
142 | TT-FG1091-I | TT | FG1091-I | #1 FURNACE REAR TEMPERATURE (I) TRANSMITTER | PD-051 | ±890 mmH2O | 1200 | 0~1200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
172 | TW-FG1090-G | TW | FG1090-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
181 | TW-FG1091-G | TW | FG1091-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
168 | TE-FG1090-G | TE | FG1090-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
177 | TE-FG1091-G | TE | FG1091-G | #1 FURNACE REAR TEMPERATURE ELEMENT (G) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
173 | TW-FG1090-H | TW | FG1090-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
182 | TW-FG1091-H | TW | FG1091-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
169 | TE-FG1090-H | TE | FG1090-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
178 | TE-FG1091-H | TE | FG1091-H | #1 FURNACE REAR TEMPERATURE ELEMENT (H) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
174 | TW-FG1090-I | TW | FG1090-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
183 | TW-FG1091-I | TW | FG1091-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
170 | TE-FG1090-I | TE | FG1090-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
179 | TE-FG1091-I | TE | FG1091-I | #1 FURNACE REAR TEMPERATURE ELEMENT (I) | PD-051 | ±890mmH2O | 1200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
15 | MCV-FA1019 | MCV | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
75 | ZSC-FA1019 | ZSC | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
98 | ZSO-FA1019 | ZSO | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
121 | ZT-FA1019 | ZT | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
48 | TS-FA1019 | TS | FA1019 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.1 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
16 | MCV-FA1020 | MCV | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
76 | ZSC-FA1020 | ZSC | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
99 | ZSO-FA1020 | ZSO | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
122 | ZT-FA1020 | ZT | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
49 | TS-FA1020 | TS | FA1020 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.2 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
17 | MCV-FA1021 | MCV | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
77 | ZSC-FA1021 | ZSC | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
100 | ZSO-FA1021 | ZSO | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
123 | ZT-FA1021 | ZT | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
50 | TS-FA1021 | TS | FA1021 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.3 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
18 | MCV-FA1022 | MCV | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
78 | ZSC-FA1022 | ZSC | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
101 | ZSO-FA1022 | ZSO | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
124 | ZT-FA1022 | ZT | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
51 | TS-FA1022 | TS | FA1022 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.4 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
19 | MCV-FA1023 | MCV | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
79 | ZSC-FA1023 | ZSC | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
102 | ZSO-FA1023 | ZSO | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
125 | ZT-FA1023 | ZT | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
52 | TS-FA1023 | TS | FA1023 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.5 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
20 | MCV-FA1024 | MCV | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
80 | ZSC-FA1024 | ZSC | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
103 | ZSO-FA1024 | ZSO | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
126 | ZT-FA1024 | ZT | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
53 | TS-FA1024 | TS | FA1024 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.6 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
21 | MCV-FA1025 | MCV | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
81 | ZSC-FA1025 | ZSC | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
104 | ZSO-FA1025 | ZSO | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
127 | ZT-FA1025 | ZT | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
54 | TS-FA1025 | TS | FA1025 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.7 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
22 | MCV-FA1026 | MCV | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | FHI |  | 0 |  | SECONDARY AIR FAN
82 | ZSC-FA1026 | ZSC | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
105 | ZSO-FA1026 | ZSO | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
128 | ZT-FA1026 | ZT | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
55 | TS-FA1026 | TS | FA1026 | #1 FURNACE REAR WALL CONTROL DAMPER MOV NO.8 TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | SECONDARY AIR FAN
147 | TW-CW1155-A1 | TW | CW1155-A1 | #1 GENERATOR AIR COOLER A-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
70 | TG-CW1155-A1 | TG | CW1155-A1 | #1 GENERATOR AIR COOLER A-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
148 | TW-CW1155-A2 | TW | CW1155-A2 | #1 GENERATOR AIR COOLER A-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
71 | TG-CW1155-A2 | TG | CW1155-A2 | #1 GENERATOR AIR COOLER A-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
149 | TW-CW1155-A3 | TW | CW1155-A3 | #1 GENERATOR AIR COOLER A-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
72 | TG-CW1155-A3 | TG | CW1155-A3 | #1 GENERATOR AIR COOLER A-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
150 | TW-CW1155-A4 | TW | CW1155-A4 | #1 GENERATOR AIR COOLER A-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
73 | TG-CW1155-A4 | TG | CW1155-A4 | #1 GENERATOR AIR COOLER A-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
151 | TW-CW1155-B1 | TW | CW1155-B1 | #1 GENERATOR AIR COOLER B-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
74 | TG-CW1155-B1 | TG | CW1155-B1 | #1 GENERATOR AIR COOLER B-1 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
152 | TW-CW1155-B2 | TW | CW1155-B2 | #1 GENERATOR AIR COOLER B-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
75 | TG-CW1155-B2 | TG | CW1155-B2 | #1 GENERATOR AIR COOLER B-1 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
153 | TW-CW1155-B3 | TW | CW1155-B3 | #1 GENERATOR AIR COOLER B-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
76 | TG-CW1155-B3 | TG | CW1155-B3 | #1 GENERATOR AIR COOLER B-2 INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
154 | TW-CW1155-B4 | TW | CW1155-B4 | #1 GENERATOR AIR COOLER B-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
77 | TG-CW1155-B4 | TG | CW1155-B4 | #1 GENERATOR AIR COOLER B-2 OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
155 | TW-CW1155-C1 | TW | CW1155-C1 | #1 GENERATOR AIR COOLER C INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
78 | TG-CW1155-C1 | TG | CW1155-C1 | #1 GENERATOR AIR COOLER C INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
156 | TW-CW1155-C2 | TW | CW1155-C2 | #1 GENERATOR AIR COOLER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
79 | TG-CW1155-C2 | TG | CW1155-C2 | #1 GENERATOR AIR COOLER C OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
157 | TW-CW1155-D1 | TW | CW1155-D1 | #1 GENERATOR AIR COOLER D INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
80 | TG-CW1155-D1 | TG | CW1155-D1 | #1 GENERATOR AIR COOLER D INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
158 | TW-CW1155-D2 | TW | CW1155-D2 | #1 GENERATOR AIR COOLER D OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
81 | TG-CW1155-D2 | TG | CW1155-D2 | #1 GENERATOR AIR COOLER D OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
74 | TW-CD1120 | TW | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
64 | TE-CD1120 | TE | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
75 | TW-CD1120(G) | TW | CD1120(G) | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
19 | TG-CD1120 | TG | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
47 | TT-CD1120 | TT | CD1120 | #1 GLAND STEAM CONDENSER OUTLET WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
52 | TW-AS1016 | TW | AS1016 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE GAUGE | PD-014 | 13 | 300 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
8 | TG-AS1016 | TG | AS1016 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE GAUGE | PD-014 | 13 | 300 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
21 | TT-AS1015 | TT | AS1015 | #1 GLAND STEAM DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER | PD-014 | 13 | 300 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
16 | XV-CD1125 | XV | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
135 | ZSC-CD1125 | ZSC | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
136 | ZSO-CD1125 | ZSO | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
16 | TCV-CD1126 | TCV | CD1126 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
47 | ZT-CD1126 | ZT | CD1126 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
19 | SV-CD1125 | SV | CD1125 | #1 GLAND STEAM DESUPERHEATER SPRAY WATER BLOCK SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
51 | TW-AS1015 | TW | AS1015 | #1 GLAND STEAM DESUPERHEATING OUTLET TEMPERATURE ELEMENT | PD-014 | 13 | 300 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
32 | TE-AS1015 | TE | AS1015 | #1 GLAND STEAM DESUPERHEATING OUTLET TEMPERATURE ELEMENT | PD-014 | 13 | 300 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
137 | ZSC-CD1126 | ZSC | CD1126 | #1 GLAND STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
138 | ZSO-CD1126 | ZSO | CD1126 | #1 GLAND STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
24 | MV-AS1393 | MV | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV | PD-014 | 13 | 300 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
90 | ZSC-AS1393 | ZSC | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
91 | ZSO-AS1393 | ZSO | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
31 | ZT-AS1393 | ZT | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
92 | TS-AS1393 | TS | AS1393 | #1 GLAND STEAM DRAIN SEPARATOR DRAIN MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
32 | LCV-HD1105-2 | LCV | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE | PD-018 | 16 & Full Vaccum | 210 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
69 | ZT-HD1105-2 | ZT | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
13 | FE-HD1105 | FE | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN FLOW ELEMENT | PD-018 | 17 & Full Vacuum | 210 | 0~69 | <1250 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
14 | FT-HD1105 | FT | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN FLOW TRANSMITTER | PD-018 | 16 & Full Vaccum | 210 | 0~69 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
49 | PG-HD1105 | PG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN PRESSURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
98 | TW-HD1105 | TW | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE ELEMENT | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
92 | TE-HD1105 | TE | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE ELEMENT | PD-018 | 16 & Full Vaccum | 210 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
99 | TW-HD1105(G) | TW | HD1105(G) | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
44 | TG-HD1105 | TG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE GAUGE | PD-018 | 16 & Full Vaccum | 210 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
69 | TT-HD1105 | TT | HD1105 | #1 HIGH PRESSURE HEATER NO.1 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 16 & Full Vaccum | 210 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
87 | TW-FW1602 | TW | FW1602 | #1 TEST WELL AT BFP INLET | PD-017 | 10 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
8 | LG-HD1105 | LG | HD1105 | #1 HIGH PRESSURE HEATER NO.1 LEVEL GAUGE | PD-018 | 16 | 210 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
13 | LS-HD1105 | LS | HD1105 | #1 HIGH PRESSURE HEATER NO.1 LEVEL SWITCH-3 | PD-018 | 16 | 210 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
11 | LT-HD1105-1 | LT | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 LEVEL TRANSMITTER-1 | PD-018 | 16 | 440 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
12 | LT-HD1105-2 | LT | HD1105-2 | #1 HIGH PRESSURE HEATER NO.1 LEVEL TRANSMITTER-2 | PD-018 | 16 | 440 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
88 | TW-FW1604 | TW | FW1604 | #1 TEST WELL AT BFP COMMON DISCHARGE | PD-017 | 230 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
89 | TW-FW1605 | TW | FW1605 | #1 TEST WELL AT BFP COMMON DISCHARGE | PD-017 | 230 | 180 | - | - | - | - | - | FHI |  | 0 |  | TW
90 | TW-FW1606 | TW | FW1606 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER | PD-017 | 230 | 220 | - | - | - | - | - | FHI |  | 0 |  | TW
91 | TW-FW1607 | TW | FW1607 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 OUTLET FEEDWATER | PD-017 | 230 | 220 | - | - | - | - | - | FHI |  | 0 |  | TW
31 | LCV-HD1105-1 | LCV | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE | PD-018 | 16 | 210 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
68 | ZT-HD1105-1 | ZT | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
50 | PG-HD1105-1 | PG | HD1105-1 | #1 HIGH PRESSURE HEATER NO.1 STEAM PRESSURE GAUGE | PD-018 | 16 | 440 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
34 | LCV-HD1106-2 | LCV | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE | PD-018 | 45 & Full Vaccum | 260 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
71 | ZT-HD1106-2 | ZT | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
35 | TW-TS1011 | TW | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-013 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
25 | TE-TS1011 | TE | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE ELEMENT | PD-013 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
36 | TW-TS1012 | TW | TS1012 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE GAUGE | PD-013 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
2 | TG-TS1012 | TG | TS1012 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE GAUGE | PD-013 | 45 | 395 | 0~600 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
14 | TT-TS1011 | TT | TS1011 | #1 HIGH PRESSURE HEATER NO.2 COLD REHEAT STEAM TEMPERATURE TRANSMITTER | PD-013 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
14 | FE-HD1106 | FE | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN FLOW ELEMENT | PD-018 | 47 & Full Vacuum | 260 | 0~45 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
15 | FT-HD1106 | FT | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN FLOW TRANSMITTER | PD-018 | 45 & Full Vaccum | 260 | 0~45 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
51 | PG-HD1106 | PG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN PRESSURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | 0~50 | - | - | - | BOURDON | FHI |  | 0 |  | PG
100 | TW-HD1106 | TW | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
93 | TE-HD1106 | TE | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 45 & Full Vaccum | 260 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
101 | TW-HD1106(G) | TW | HD1106(G) | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
45 | TG-HD1106 | TG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 45 & Full Vaccum | 260 | 0~300 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
70 | TT-HD1106 | TT | HD1106 | #1 HIGH PRESSURE HEATER NO.2 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 45 & Full Vaccum | 260 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
92 | TW-FW1609 | TW | FW1609 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER | PD-017 | 230 | 275 | - | - | - | - | - | FHI |  | 0 |  | TW
9 | LG-HD1106 | LG | HD1106 | #1 HIGH PRESSURE HEATER NO.2 LEVEL GAUGE | PD-018 | 45 | 260 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
14 | LS-HD1106 | LS | HD1106 | #1 HIGH PRESSURE HEATER NO.2 LEVEL SWITCH-3 | PD-018 | 45 | 260 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
13 | LT-HD1106-1 | LT | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 LEVEL TRANSMITTER-1 | PD-018 | 45 | 395 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
14 | LT-HD1106-2 | LT | HD1106-2 | #1 HIGH PRESSURE HEATER NO.2 LEVEL TRANSMITTER-2 | PD-018 | 45 | 395 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
93 | TW-FW1610 | TW | FW1610 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 OUTLET FEEDWATER | PD-017 | 230 | 275 | - | - | - | - | - | FHI |  | 0 |  | TW
9 | VT-FW1115-A11 | VT | FW1115-A11 | #1 BFP(A) PUMP CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
10 | VT-FW1115-A12 | VT | FW1115-A12 | #1 BFP(A) PUMP CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
11 | VT-FW1115-A21 | VT | FW1115-A21 | #1 BFP(A) PUMP CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
33 | LCV-HD1106-1 | LCV | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE | PD-018 | 45 | 260 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
70 | ZT-HD1106-1 | ZT | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
52 | PG-HD1106-1 | PG | HD1106-1 | #1 HIGH PRESSURE HEATER NO.2 STEAM PRESSURE GAUGE | PD-018 | 45 | 395 | 0~50 | - | - | - | BOURDON | FHI |  | 0 |  | PG
20 | ZSF-SB1040 | ZSF | SB1040 | #1 HOT END SOOTBLOWER LANCE EXTEND LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
22 | ZSR-SB1040 | ZSR | SB1040 | #1 HOT END SOOTBLOWER LANCE PARK LIMIT SWITCH | - | - | - | - | DI | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
4 | PT-SB1040 | PT | SB1040 | #1 HOT END SOOTBLOWER STEAM PRESSURE TRANSMITTER | - | - | - | 0~16Kg/c㎡G | AI 4~20mA | FIELD | LCP | - | PACKAGE (AIR PRE HEATER) |  | 0 |  | AIR PREHEATER
4 | MV-HR1391 | MV | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV | PD-012 | 45 | 550 | - | DO | DCS | FIELD | DC TYPE | FHI |  | 0 |  | MV
28 | ZSC-HR1391 | ZSC | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
29 | ZSO-HR1391 | ZSO | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
7 | ZT-HR1391 | ZT | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV POSITION TRANSMITTER | PD-012 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
30 | TS-HR1391 | TS | HR1391 | #1 HOT REHEAT STEAM BLOW-OFF MOV TORQUE SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
33 | TW-HR1902 | TW | HR1902 | #1 HOT REHEAT STEAM TEMPERATURE | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
2 | PCV-MS1020 | PCV | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE | PD-011 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
10 | ZSC-MS1020 | ZSC | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
11 | ZSO-MS1020 | ZSO | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
3 | ZT-MS1020 | ZT | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
4 | SV-MS1020 | SV | MS1020 | #1 HP TURBINE BYPASS CONTROL VALVE SOLENOID VALVE (QUICK OPEN) | PD-011 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
12 | VT-FW1115-A22 | VT | FW1115-A22 | #1 BFP(A) PUMP CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
13 | VT-FW1115-A31 | VT | FW1115-A31 | #1 BFP(A) MOTOR CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
14 | VT-FW1115-A32 | VT | FW1115-A32 | #1 BFP(A) MOTOR CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
15 | VT-FW1115-A41 | VT | FW1115-A41 | #1 BFP(A) MOTOR CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
16 | VT-FW1115-A42 | VT | FW1115-A42 | #1 BFP(A) MOTOR CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
17 | VT-FW1115-B11 | VT | FW1115-B11 | #1 BFP(B) PUMP CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
18 | VT-FW1115-B12 | VT | FW1115-B12 | #1 BFP(B) PUMP CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
19 | VT-FW1115-B21 | VT | FW1115-B21 | #1 BFP(B) PUMP CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
20 | VT-FW1115-B22 | VT | FW1115-B22 | #1 BFP(B) PUMP CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
4 | XV-MS1023 | XV | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE | PD-011 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
12 | ZSC-MS1023 | ZSC | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
13 | ZSO-MS1023 | ZSO | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
5 | SV-MS1023 | SV | MS1023 | #1 HP TURBINE BYPASS OUTLET DRAIN POT DP-MS02 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
4 | PT-MS1021 | PT | MS1021 | #1 HP TURBINE BYPASS OUTLET PRESSURE TRANSMITTER | PD-011 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
8 | TW-MS1022-1 | TW | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-011 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
14 | TE-MS1022-1 | TE | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-011 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
9 | TW-MS1022-2 | TW | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-011 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
15 | TE-MS1022-2 | TE | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-011 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
4 | TT-MS1022-1 | TT | MS1022-1 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-1 | PD-011 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
5 | TT-MS1022-2 | TT | MS1022-2 | #1 HP TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-2 | PD-011 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
7 | XV-HR1022 | XV | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
24 | ZSC-HR1021 | ZSC | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
25 | ZSO-HR1021 | ZSO | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
26 | ZSC-HR1022 | ZSC | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
27 | ZSO-HR1022 | ZSO | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE DRAIN VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
9 | SV-HR1022 | SV | HR1022 | #1 ILP TURBINE LINE DRAIN POT DP-HR02 DRAIN VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
6 | XV-HR1021 | XV | HR1021 | #1 ILP TURBINE LINE DRAIN POT DP-HR01 DRAIN VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
8 | SV-HR1021 | SV | HR1021 | #1 ILP TURBINE LINEDRAIN POT DP-HR01 DRAIN VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
5 | PCD-FG1056-1 | PCD | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE CONTROL DAMPER | PD-051 | - | - | - | AO 4~20mA | DCS | FIELD | MODULATING | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
34 | ZT-FG1056-1 | ZT | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE CONTROL DAMPER POSITION TRANSMITTER | PD-051 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
30 | ZSC-FG1056-1 | ZSC | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE PNEUMATIC CONTROL DAMPER CLOSE POSITION SWITCH | PD-051 | - | - | - | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
32 | ZSO-FG1056-1 | ZSO | FG1056-1 | #1 INDUCED DRAFT FAN DISCHARGE PNEUMATIC CONTROL DAMPER OPEN POSITION SWITCH | PD-051 | - | - | - | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
12 | TE-FG1056-1 | TE | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
117 | TT-FG1056-1 | TT | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
26 | VT-FG1056-1 | VT | FG1056-1 | #1 INDUCED DRAFT FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
31 | ZSC-LO1756 | ZSC | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING COUPLING SCOOP TUBE POSITION(0%) | PD-051 | - | - | - | DI | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
10 | SE-LO1756 | SE | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING PICK UP SPEED | PD-051 | - | - | - | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
11 | ST-LO1756 | ST | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING PICK UP SPEED TRANSMITTER | PD-051 | - | - | 1200rpm | WET 4~20mA | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
35 | ZT-LO1756 | ZT | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING SCOOP TUBE POSITION TRANSMITTER | PD-051 | - | - | 0~100% | WET 4~21mA | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
33 | ZSO-LO1756 | ZSO | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING SCOOP TUBE POSITION(100%) | PD-051 | - | - | - | DI | LCP | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
1 | DPG-LO1756-1 | DPG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE GAUGE (MAINTENANCE) | PD-051 | - | - | 0.61 Kg/c㎡ | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
2 | DPG-LO1756-2 | DPG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE GAUGE OF DUPLEX FILTER | PD-051 | - | - | 0~1.1 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 1 |  | INDUCED DRAFT FAN
3 | DPS-LO1756 | DPS | LO1756 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL DIFFERENTIAL PRESSURE SWITCH HIGH OF DUPLEX FILTER | PD-051 | - | - | 0.20~2.04 Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
7 | PG-LO1756-2 | PG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL PRESSURE GAUGE AT DOWNSTREAM OF LUBE OIL ORIFICE | PD-051 | - | - | 0~1.1 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
6 | PG-LO1756-1 | PG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL PRESSURE GAUGE AT UPSTREAM OF COUPLING | PD-051 | - | - | 0~4.08 Kg/c㎡G | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
23 | TG-LO1756-2 | TG | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE GAUGE AT DOWNSTREAM OF HEAT EXCHANGER | PD-051 | - | - | 0~150℃ | - | - | - | BI-METAL | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
22 | TG-LO1756-1 | TG | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE GAUGE AT UPSTREAM OF HEAT EXCHANGER | PD-051 | - | - | 0~150℃ | - | - | - | BI-METAL | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
24 | TS-LO1756-1 | TS | LO1756-1 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE SWITCH HIGH | PD-051 | - | - | 0~160℃ | DI | FIELD | DCS | CAPILLIARY | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
25 | TS-LO1756-2 | TS | LO1756-2 | #1 INDUCED DRAFT FAN HYDRAULIC COUPLING WORKING OIL TEMPERATURE SWITCH HIGH-HIGH | PD-051 | - | - | 0~160℃ | DI | FIELD | ARP | CAPILLIARY | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
66 | PT-FG1141-A | PT | FG1141-A | #1 INDUCED DRAFT FAN INLET FLUE GAS PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
67 | PT-FG1141-B | PT | FG1141-B | #1 INDUCED DRAFT FAN INLET FLUE GAS PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 200 | -600~0 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
8 | PSL-LO1756 | PSL | LO1756 | #1 INDUCED DRAFT FAN LUBE OIL PRESSURE SWITCH LOW AT DOWNSTREAM OF LUBE OIL FILTER | PD-051 | - | - | 0~2.55 Kg/c㎡G | DI | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
9 | PSLL-LO1756 | PSLL | LO1756 | #1 INDUCED DRAFT FAN LUBE OIL PRESSURE SWITCH LOW-LOW AT DOWNSTREAM OF LUBE OIL FILTER | PD-051 | - | - | 0~2.55 Kg/c㎡G | DI | FIELD | ARP | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
15 | TE-FG1056-4 | TE | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
120 | TT-FG1056-4 | TT | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
29 | VT-FG1056-4 | VT | FG1056-4 | #1 INDUCED DRAFT FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
14 | TE-FG1056-3 | TE | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
28 | VT-FG1056-3 | VT | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
119 | TT-FG1056-3 | TT | FG1056-3 | #1 INDUCED DRAFT FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
122 | TT-FG1056-V | TT | FG1056-V | #1 INDUCED DRAFT FAN MOTOR WINDIING (V) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
16 | TE-FG1056-U1 | TE | FG1056-U1 | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
17 | TE-FG1056-U2 | TE | FG1056-U2 | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
121 | TT-FG1056-U | TT | FG1056-U | #1 INDUCED DRAFT FAN MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
18 | TE-FG1056-V1 | TE | FG1056-V1 | #1 INDUCED DRAFT FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
19 | TE-FG1056-V2 | TE | FG1056-V2 | #1 INDUCED DRAFT FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
20 | TE-FG1056-W1 | TE | FG1056-W1 | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
21 | TE-FG1056-W2 | TE | FG1056-W2 | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
123 | TT-FG1056-W | TT | FG1056-W | #1 INDUCED DRAFT FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
13 | TE-FG1056-2 | TE | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING TEMPERATURE | PD-051 | - | - | - | - | FIELD | TT | RTD | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
118 | TT-FG1056-2 | TT | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-051 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
27 | VT-FG1056-2 | VT | FG1056-2 | #1 INDUCED DRAFT FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-051 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
4 | LG-LO1756-2 | LG | LO1756-2 | #1 INDUCED DRAFT FAN OIL LEVEL GAUGE | PD-051 | - | - | - | - | - | - | - | PACKAGE (IDF) |  | 0 |  | INDUCED DRAFT FAN
68 | PT-FG1151 | PT | FG1151 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS PRESSURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | -600~600 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
207 | TW-FG1152 | TW | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
203 | TE-FG1152 | TE | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
166 | TT-FG1152 | TT | FG1152 | #1 INDUCED DRAFT FAN OUTLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
88 | PG-PA0706A | PG | PA0706A | #1 INSTRUMENT AIR TANK T-0706A PRESSURE GAUGE | PD-023,2/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
89 | PG-PA0706B | PG | PA0706B | #1 INSTRUMENT AIR TANK T-0706B PRESSURE GAUGE | PD-023,2/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
26 | LCV-HD1101-2 | LCV | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
63 | ZT-HD1101-2 | ZT | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
30 | MV-CD1003 | MV | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV | PD-016 | 24 | 150 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
112 | ZSC-CD1003 | ZSC | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
113 | ZSO-CD1003 | ZSO | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
38 | ZT-CD1003 | ZT | CD1003 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE BYPASS SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
28 | MV-CD1001 | MV | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
106 | ZSC-CD1001 | ZSC | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
107 | ZSO-CD1001 | ZSO | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
36 | ZT-CD1001 | ZT | CD1001 | #1 LOW PRESSURE HEATER NO.1 CONDENSATE INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
29 | MV-CD1002 | MV | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV | PD-016 | 24 | 150 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
109 | ZSC-CD1002 | ZSC | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
110 | ZSO-CD1002 | ZSO | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
37 | ZT-CD1002 | ZT | CD1002 | #1 LOW PRESSURE HEATER NO.1 CONDESATE OUTLET SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
57 | TW-CD1101 | TW | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
35 | TE-CD1101 | TE | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
24 | TT-CD1101 | TT | CD1101 | #1 LOW PRESSURE HEATER NO.1 INLET CONDENSATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
11 | PG-CD1101-1 | PG | CD1101-1 | #1 LOW PRESSURE HEATER NO.1 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 65 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
5 | LG-HD1101 | LG | HD1101 | #1 LOW PRESSURE HEATER NO.1 LEVEL GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
10 | LS-HD1101 | LS | HD1101 | #1 LOW PRESSURE HEATER NO.1 LEVEL SWITCH-3 | PD-018 | Full Vaccum & 3.6 | 150 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
5 | LT-HD1101-1 | LT | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 LEVEL TRANSMITTER-1 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
6 | LT-HD1101-2 | LT | HD1101-2 | #1 LOW PRESSURE HEATER NO.1 LEVEL TRANSMITTER-2 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
12 | PG-CD1101-2 | PG | CD1101-2 | #1 LOW PRESSURE HEATER NO.1 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
25 | LCV-HD1101-1 | LCV | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
62 | ZT-HD1101-1 | ZT | HD1101-1 | #1 LOW PRESSURE HEATER NO.1 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
44 | PG-HD1101 | PG | HD1101 | #1 LOW PRESSURE HEATER NO.1 STEAM PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
25 | PT-HD1101 | PT | HD1101 | #1 LOW PRESSURE HEATER NO.1 STEAM PRESSURE TRANSMITTER | PD-018 | 3.5 & Full Vacuum | 150 | -1~5 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
28 | LCV-HD1102-2 | LCV | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
65 | ZT-HD1102-2 | ZT | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
11 | FE-HD1102 | FE | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN FLOW ELEMENT | PD-018 | 3.6 & Full Vacuum | 150 | 0~27.5 | <125 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
12 | FT-HD1102 | FT | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN FLOW TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 150 | 0~27.5 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
45 | PG-HD1102 | PG | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
94 | TW-HD1102 | TW | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
90 | TE-HD1102 | TE | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 150 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
95 | TW-HD1102(G) | TW | HD1102(G) | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
42 | TG-HD1102 | TG | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 150 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
67 | TT-HD1102 | TT | HD1102 | #1 LOW PRESSURE HEATER NO.2 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
13 | PG-CD1102-1 | PG | CD1102-1 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
58 | TW-CD1102 | TW | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
36 | TE-CD1102 | TE | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
25 | TT-CD1102 | TT | CD1102 | #1 LOW PRESSURE HEATER NO.2 INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
6 | LG-HD1102 | LG | HD1102 | #1 LOW PRESSURE HEATER NO.2 LEVEL GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
11 | LS-HD1102 | LS | HD1102 | #1 LOW PRESSURE HEATER NO.2 LEVEL SWITCH-3 | PD-018 | Full Vaccum & 3.6 | 150 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
7 | LT-HD1102-1 | LT | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 LEVEL TRANSMITTER-1 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
8 | LT-HD1102-2 | LT | HD1102-2 | #1 LOW PRESSURE HEATER NO.2 LEVEL TRANSMITTER-2 | PD-018 | Full Vaccum & 3.6 | 150 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
14 | PG-CD1102-2 | PG | CD1102-2 | #1 LOW PRESSURE HEATER NO.2 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
27 | LCV-HD1102-1 | LCV | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 150 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
64 | ZT-HD1102-1 | ZT | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
46 | PG-HD1102-1 | PG | HD1102-1 | #1 LOW PRESSURE HEATER NO.2 STEAM PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 150 | -1~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
30 | LCV-HD1103-2 | LCV | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 ALTERNATE DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 200 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
67 | ZT-HD1103-2 | ZT | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 ALTERNATE DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
12 | FE-HD1103 | FE | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN FLOW ELEMENT | PD-018 | 3.6 & Full Vacuum | 200 | 0~15 | <1200 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
13 | FT-HD1103 | FT | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN FLOW TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 200 | 0~15 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
47 | PG-HD1103 | PG | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN PRESSURE GAUGE | PD-018 | Full Vaccum & 3.6 | 200 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
96 | TW-HD1103 | TW | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
91 | TE-HD1103 | TE | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE ELEMENT | PD-018 | 3.6 & Full Vaccum | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
97 | TW-HD1103(G) | TW | HD1103(G) | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
43 | TG-HD1103 | TG | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE GAUGE | PD-018 | 3.6 & Full Vaccum | 200 | 0~200 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
68 | TT-HD1103 | TT | HD1103 | #1 LOW PRESSURE HEATER NO.3 DRAIN TEMPERATURE TRANSMITTER | PD-018 | 3.6 & Full Vaccum | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
15 | PG-CD1103-1 | PG | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 150 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
59 | TW-CD1103-1 | TW | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
37 | TE-CD1103-1 | TE | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 150 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
26 | TT-CD1103-1 | TT | CD1103-1 | #1 LOW PRESSURE HEATER NO.3 INLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 150 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
7 | LG-HD1103 | LG | HD1103 | #1 LOW PRESSURE HEATER NO.3 LEVEL GAUGE | PD-018 | 3.6 | 200 | 0~200 | - | - | - | REFLEX | FHI |  | 0 |  | LG
12 | LS-HD1103 | LS | HD1103 | #1 LOW PRESSURE HEATER NO.3 LEVEL SWITCH-3 | PD-018 | 3.6 | 200 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
9 | LT-HD1103-1 | LT | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 LEVEL TRANSMITTER-1 | PD-018 | 3.6 | 210 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
10 | LT-HD1103-2 | LT | HD1103-2 | #1 LOW PRESSURE HEATER NO.3 LEVEL TRANSMITTER-2 | PD-018 | 3.6 | 210 | 0~610 | AI 4~20mA | FIELD | DCS | GUIDE WAVE RADAR | FHI |  | 0 |  | LT
16 | PG-CD1103-2 | PG | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE PRESSURE GAUGE | PD-016 | 24 | 200 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
60 | TW-CD1103-2 | TW | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
38 | TE-CD1103-2 | TE | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE ELEMENT | PD-016 | 24 | 200 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
27 | TT-CD1103-2 | TT | CD1103-2 | #1 LOW PRESSURE HEATER NO.3 OUTLET CONDESATE TEMPERATURE TRANSMITTER | PD-016 | 24 | 200 | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
29 | LCV-HD1103-1 | LCV | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 PRIMARY DRAIN VALVE | PD-018 | 3.6 & Full Vaccum | 200 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
66 | ZT-HD1103-1 | ZT | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 PRIMARY DRAIN VALVE POSITION TRANSMITTER | PD-018 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
48 | PG-HD1103-1 | PG | HD1103-1 | #1 LOW PRESSURE HEATER NO.3 STEAM PRESSURE GAUGE | PD-018 | 3.6 | 210 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
12 | TT-HR1012-1 | TT | HR1012-1 | #1 LOW PRESSURE TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 15 | 280 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
13 | TT-HR1012-2 | TT | HR1012-2 | #1 LOW PRESSURE TURBINE BYPASS OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 15 | 280 | 0~300 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
114 | TS-CD1003 | TS | CD1003 | #1 LP HEATER NO.1 CONDENSATE BYPASS MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
108 | ZSC-CD1001 | ZSC | CD1001 | #1 LP HEATER NO.1 INLET CONDENSATE SHUT-OFF MOV CLOSE POSITION TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
111 | TS-CD1002 | TS | CD1002 | #1 LP HEATER NO.1 OUTLET CONDESATE SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
3 | PCV-HR1010 | PCV | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE | PD-012 | 45 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
20 | ZSC-HR1010 | ZSC | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE CLOSE POSITION SWITCH | PD-012 | - | - | #VALUE! | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
21 | ZSO-HR1010 | ZSO | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
25 | TW-HR1010 | TW | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OUTLET TEMPERATURE ELEMENT | PD-012 | - | - | - | - | - | - | - | PACKAGE (CV) | NEW ADDED | 0 |  | TW
22 | TE-HR1010 | TE | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE OUTLET TEMPERATURE ELEMENT | PD-012 | - | - | - | - | FIELD | TT | T/C | PACKAGE (CV) | NEW ADDED | 0 |  | TE
6 | ZT-HR1010 | ZT | HR1010 | #1 LP TURBINE BYPASS CONTROL VALVE POSITION TRANSMITTER | PD-012 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
14 | XV-CD1114 | XV | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
16 | SV-CD1114 | SV | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
142 | ZSC-CD1114 | ZSC | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
143 | ZSO-CD1114 | ZSO | CD1114 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
14 | TCV-CD1115 | TCV | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
129 | ZSC-CD1115 | ZSC | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
130 | ZSO-CD1115 | ZSO | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
43 | ZT-CD1115 | ZT | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
17 | SV-CD1115 | SV | CD1115 | #1 LP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE SOLENOID VALVE(QUICK OPEN) | PD-016 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
10 | PT-HR1011 | PT | HR1011 | #1 LP TURBINE BYPASS OUTLET PRESSURE TRANSMITTER | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
26 | TW-HR1012-1 | TW | HR1012-1 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 15 | 280 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
23 | TE-HR1012-1 | TE | HR1012-1 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 15 | 280 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
27 | TW-HR1012-2 | TW | HR1012-2 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 15 | 280 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
24 | TE-HR1012-2 | TE | HR1012-2 | #1 LP TURBINE BYPASS OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 15 | 280 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
2 | FE-CD1115 | FE | CD1115 | #1 LP TURBINE BYPASS SPRAY WATER FLOW ELEMENT | PD-016 | 24 | 65 | 0~46 | <2500 | - | - | ORIFICE PLATE | FHI |  | 0 |  | FE
2 | FT-CD1115 | FT | CD1115 | #1 LP TURBINE BYPASS SPRAY WATER FLOW TRANSMITTER | PD-016 | 24 | 65 | 0~46 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
6 | SV-HR1010 | SV | HR1010 | #1 LP TURBINE BYPASS VALVE SOLENOID VALVE(QUICK OPEN) | PD-012 | - | - | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
5 | XV-HR1010-1 | XV | HR1010-1 | #1 LP TURBINE BYPASS VALVE WARMING VALVE | PD-012 | 45 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
7 | SV-HR1010-1 | SV | HR1010-1 | #1 LP TURBINE BYPASS VALVE WARMING VALVE SOLENOID VALVE | PD-012 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
22 | ZSC-HR1010-1 | ZSC | HR1010-1 | #1 LP TURBINE BYPASS WARMING VALVE CLOSE POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
23 | ZSO-HR1010-1 | ZSO | HR1010-1 | #1 LP TURBINE BYPASS WARMING VALVE OPEN POSITION SWITCH | PD-012 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
1 | PCV-MS1001 | PCV | MS1001 | #1 MAIN STEAM BLOW OFF VALVE | PD-011 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
2 | ZT-MS1001 | ZT | MS1001 | #1 MAIN STEAM BLOW OFF VALVE POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
49 | TW-AS1002 | TW | AS1002 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE GAUGE | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
7 | TG-AS1002 | TG | AS1002 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE GAUGE | PD-014 | 13 | 390 | 0~600 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
19 | TT-AS1001 | TT | AS1001 | #1 MAIN STEAM DESUPERHEATER DOWNSTREAM TEMPERATURE TRANSMITTER | PD-014 | 13 | 390 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
48 | TW-AS1001 | TW | AS1001 | #1 MAIN STEAM DESUPERHEATING DOWNSTREAM TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
30 | TE-AS1001 | TE | AS1001 | #1 MAIN STEAM DESUPERHEATING DOWNSTREAM TEMPERATURE ELEMENT | PD-014 | 13 | 390 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
21 | AT-SP1021 | AT | SP1021 | #1 MAIN STEAM LINE CATION CONDUCTIVITY | PD-044 | 144 | 550 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
3 | XV-MS1011 | XV | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE | PD-011 | 144 | 550 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
8 | ZSC-MS1011 | ZSC | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
9 | ZSO-MS1011 | ZSO | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
3 | SV-MS1011 | SV | MS1011 | #1 MAIN STEAM LINE DRAIN POT DP-MS01 DRAIN VALVE SOLENOID VALVE | PD-011 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
23 | FG-SP1021 | FG | SP1021 | #1 MAIN STEAM LINE FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
18 | FG-SP1016 | FG | SP1016 | #1 MAIN STEAM LINE FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
19 | FG-SP1017 | FG | SP1017 | #1 MAIN STEAM LINE FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
127 | PG-SP1007 | PG | SP1007 | #1 MAIN STEAM LINE PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
93 | TG-SP1007 | TG | SP1007 | #1 MAIN STEAM LINE THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
16 | AT-SP1016 | AT | SP1016 | #1 MAIN STEAM PH | PD-044 | 144 | 550 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
2 | PT-MS1006-1 | PT | MS1006-1 | #1 MAIN STEAM PRESSURE TRANSMITTER-1 | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
3 | PT-MS1006-2 | PT | MS1006-2 | #1 MAIN STEAM PRESSURE TRANSMITTER-2 | PD-011 | 144 | 550 | 0~150 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
2 | MV-MS1391 | MV | MS1391 | #1 MAIN STEAM SHUT-OFF MOV | PD-011 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
14 | ZSC-MS1391 | ZSC | MS1391 | #1 MAIN STEAM SHUT-OFF MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
15 | ZSO-MS1391 | ZSO | MS1391 | #1 MAIN STEAM SHUT-OFF MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
4 | ZT-MS1391 | ZT | MS1391 | #1 MAIN STEAM SHUT-OFF MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
16 | TS-MS1391 | TS | MS1391 | #1 MAIN STEAM SHUT-OFF MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
3 | MV-MS1392 | MV | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV | PD-011 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
17 | ZSC-MS1392 | ZSC | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
18 | ZSO-MS1392 | ZSO | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
5 | ZT-MS1392 | ZT | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
19 | TS-MS1392 | TS | MS1392 | #1 MAIN STEAM SHUT-OFF VALVE BYPASS MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
17 | AT-SP1017 | AT | SP1017 | #1 MAIN STEAM SILICA | PD-044 | 144 | 550 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
7 | TW-MS1007 | TW | MS1007 | #1 MAIN STEAM TEMPERATURE ELEMENT | PD-011 | 144 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
13 | TE-MS1007 | TE | MS1007 | #1 MAIN STEAM TEMPERATURE ELEMENT | PD-011 | 144 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
3 | TT-MS1007 | TT | MS1007 | #1 MAIN STEAM TEMPERATURE TRANSMITTER | PD-011 | 144 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
15 | XV-CD1123 | XV | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-016 | 24 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
18 | SV-CD1123 | SV | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE SOLENOID VALVE | PD-016 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
131 | ZSC-CD1123 | ZSC | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
132 | ZSO-CD1123 | ZSO | CD1123 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
15 | TCV-CD1124 | TCV | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE | PD-016 | 24 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
133 | ZSC-CD1124 | ZSC | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
134 | ZSO-CD1124 | ZSO | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
46 | ZT-CD1124 | ZT | CD1124 | #1 MAIN STEAM TO AUXILIARY STEAM DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
22 | MV-AS1391 | MV | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV | PD-014 | 144 | 550 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
84 | ZSC-AS1391 | ZSC | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
85 | ZSO-AS1391 | ZSO | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
29 | ZT-AS1391 | ZT | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
86 | TS-AS1391 | TS | AS1391 | #1 MAIN STEAM TO AUXILIARY STEAM HEADER SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
4 | PCV-AS1010 | PCV | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE | PD-014 | 144 | 550 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
82 | ZSC-AS1010 | ZSC | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
83 | ZSO-AS1010 | ZSO | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
25 | ZT-AS1010 | ZT | AS1010 | #1 MAIN STEAM TO AUXILIARY STEAM SUPPLY PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
9 | FG-SP1007 | FG | SP1007 | #1 MAKE-UP WATER PUMP OUTLET FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
8 | FG-SP1006 | FG | SP1006 | #1 MAKE-UP WATER PUMP OUTLET FLOWMETER FOR pH SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
10 | FG-SP1008 | FG | SP1008 | #1 MAKE-UP WATER PUMP OUTLET FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
123 | PG-SP1003 | PG | SP1003 | #1 MAKE-UP WATER PUMP OUTLET PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
89 | TG-SP1003 | TG | SP1003 | #1 MAKE-UP WATER PUMP OUTLET THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
6 | AT-SP1006 | AT | SP1006 | #1 MAKE-UP WATER PUMP OUTLET WATER PH | PD-044 | 10 | 65 | 0~14 | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
8 | AT-SP1008 | AT | SP1008 | #1 MAKE-UP WATER PUMP OUTLET WATER SILICA | PD-044 | 10 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
7 | AT-SP1007 | AT | SP1007 | #1 MAKE-UP WATER PUMP OUTLET WATER SPECIFIC CONDUCTIVITY | PD-044 | 10 | 65 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
33 | MV-MU1001 | MV | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV | PD-016 | 10 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
139 | ZSC-MU1001 | ZSC | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
140 | ZSO-MU1001 | ZSO | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
48 | ZT-MU1001 | ZT | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
141 | TS-MU1001 | TS | MU1001 | #1 MAKE-UP WATER TO CONDENSER SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
23 | XV-MU1109 | XV | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE | PD-021 | 10 | 65 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
202 | ZSC-MU1109 | ZSC | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE CLOSE POSITION SWITCH | PD-021 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
201 | ZSO-MU1109 | ZSO | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE OPEN POSITION SWITCH | PD-021 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
27 | SV-MU1109 | SV | MU1109 | #1 MAKE-UP WATER TO EXPANSION TANK ON/OFF VALVE SOLENOID VALVE | PD-021 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
20 | DPT-FG1083 | DPT | FG1083 | #1 MIDDLE/UPPER FURNACE DIFFERENTIAL PRESSURE TRANSMITTER-1 | PD-051 | ±890 mmH2O | 1200 | -1500~1500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
22 | DPT-FG1183 | DPT | FG1183 | #1 MIDDLE/UPPER FURNACE DIFFERENTIAL PRESSURE TRANSMITTER-2 | PD-051 | ±890 mmH2O | 1200 | -1500~1500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI | NEW ADDED | 0 |  | DPT
39 | LSH-CH1103 | LSH | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
38 | LSL-CH1103 | LSL | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
37 | LSLL-CH1103 | LSLL | CH1103 | #1 NEUTRAL AMINE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
18 | DPT-FG1081 | DPT | FG1081 | #1 OVERALL FURNACE DIFFERENTIAL PRESSURE TRANSMITTER (A) | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
19 | DPT-FG1082 | DPT | FG1082 | #1 OVERALL FURNACE DIFFERENTIAL PRESSURE TRANSMITTER (B) | PD-051 | ±890 mmH2O | 1200 | 0~2500 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
86 | PG-PA0705A | PG | PA0705A | #1 PLANT AIR TANK T-0705A PRESSURE GAUGE | PD-023,1/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
87 | PG-PA0705B | PG | PA0705B | #1 PLANT AIR TANK T-0705B PRESSURE GAUGE | PD-023,1/6 | 10 | 60 | 0~10 | - | - | - | - | PACKAGE (COMPRESSOR) |  | 0 |  | PG
32 | MV-CD1008 | MV | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV | PD-016 | 24 | 65 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
124 | ZSC-CD1008 | ZSC | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
125 | ZSO-CD1008 | ZSO | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV OPEN POSITION SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
40 | ZT-CD1008 | ZT | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV POSITION TRANSMITTER | PD-016 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
126 | TS-CD1008 | TS | CD1008 | #1 POLISHER TO CONDENSATE SHUT-OFF MOV TORQUE SWITCH | PD-016 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
2 | TE-FA1053-1 | TE | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
167 | TT-FA1053-1 | TT | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
13 | VT-FA1053-1 | VT | FA1053-1 | #1 PRIMARY AIR FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
19 | FE-FA1071 | FE | FA1071 | #1 PRIMARY AIR FAN INLET AIR FLOW ELEMENT | PD-052 | 0 | 66 | - | - | - | - | VENTURI | PACKAGE (PAF) |  | 0 |  | FE
21 | FT-FA1071 | FT | FA1071 | #1 PRIMARY AIR FAN INLET AIR FLOW TRANSMITTER | PD-052 | 0 | 66 | 0~648 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
208 | TW-FA1072 | TW | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-052 | 0 | 66 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
204 | TE-FA1072 | TE | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-052 | 0 | 66 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
174 | TT-FA1072 | TT | FA1072 | #1 PRIMARY AIR FAN INLET AIR TEMPERATURE TRANSMITTER | PD-052 | 0 | 66 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
1 | MCV-FA1053-1 | MCV | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV | PD-052 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
19 | ZT-FA1053-1 | ZT | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-052 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
17 | ZSC-FA1053-1 | ZSC | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
18 | ZSO-FA1053-1 | ZSO | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
12 | TS-FA1053-1 | TS | FA1053-1 | #1 PRIMARY AIR FAN INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-052 | - | - | - | DI | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
1 | DPS-LO1753 | DPS | LO1753 | #1 PRIMARY AIR FAN INLET FILTER DIFFERENTIAL PRESSURE SWITCH | PD-052 | - | - | 0~10Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
2 | LSL-LO1753 | LSL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL LEVEL SWITCH | PD-052 | - | - | 270L(<240L) | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
3 | LSLL-LO1753 | LSLL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL LEVEL SWITCH | PD-052 | - | - | 270L(<200L) | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
4 | PG-LO1753-1 | PG | LO1753-1 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-1 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
5 | PG-LO1753-2 | PG | LO1753-2 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-2 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
6 | PG-LO1753-3 | PG | LO1753-3 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-3 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
7 | PG-LO1753-4 | PG | LO1753-4 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-4 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
8 | PG-LO1753-5 | PG | LO1753-5 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-5 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
9 | PG-LO1753-6 | PG | LO1753-6 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE GAUGE-6 | PD-052 | - | - | 0~10Kg/cm2 | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
11 | PSLL-LO1753 | PSLL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE LOW LOW SWITCH | PD-052 | - | - | 0~6Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
10 | PSL-LO1753 | PSL | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM PRESSURE LOW SWITCH | PD-052 | - | - | 0~10Kg/cm2 | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
12 | TG-LO1753 | TG | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM TEMPERATURE GAUGE | PD-052 | - | - | 0~100℃ | - | - | - |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
13 | TS-LO1753 | TS | LO1753 | #1 PRIMARY AIR FAN LUBE OIL SYSTEM TEMPERATURE SWITCH | PD-052 | - | - | 0~200℃ | DI | FIELD | DCS |  | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN LUBE OIL
5 | TE-FA1053-4 | TE | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
170 | TT-FA1053-4 | TT | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
16 | VT-FA1053-4 | VT | FA1053-4 | #1 PRIMARY AIR FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
4 | TE-FA1053-3 | TE | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
15 | VT-FA1053-3 | VT | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
169 | TT-FA1053-3 | TT | FA1053-3 | #1 PRIMARY AIR FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
6 | TE-FA1053-U1 | TE | FA1053-U1 | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
7 | TE-FA1053-U2 | TE | FA1053-U2 | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
171 | TT-FA1053-U | TT | FA1053-U | #1 PRIMARY AIR FAN MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
8 | TE-FA1053-V1 | TE | FA1053-V1 | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
9 | TE-FA1053-V2 | TE | FA1053-V2 | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
172 | TT-FA1053-V | TT | FA1053-V | #1 PRIMARY AIR FAN MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
10 | TE-FA1053-W1 | TE | FA1053-W1 | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
11 | TE-FA1053-W2 | TE | FA1053-W2 | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
173 | TT-FA1053-W | TT | FA1053-W | #1 PRIMARY AIR FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
3 | TE-FA1053-2 | TE | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING TEMPERATURE | PD-052 | - | - | - | - | FIELD | TT | RTD | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
168 | TT-FA1053-2 | TT | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-052 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
14 | VT-FA1053-2 | VT | FA1053-2 | #1 PRIMARY AIR FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-052 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (PAF) |  | 0 |  | PRIMARY AIR FAN
69 | PT-FA1075 | PT | FA1075 | #1 PRIMARY AIR PREHEATER INLET AIR PRESSURE TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
175 | TT-FA1073 | TT | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE (A) TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
176 | TT-FA1074 | TT | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE (B) TRANSMITTER | PD-052 | -340~2500 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
209 | TW-FA1073 | TW | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
205 | TE-FA1073 | TE | FA1073 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
210 | TW-FA1074 | TW | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-052 | -340~2500 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
206 | TE-FA1074 | TE | FA1074 | #1 PRIMARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-052 | -340~2500 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
70 | PT-FA1078 | PT | FA1078 | #1 PRIMARY AIR PREHEATER OUTLET AIR PRESSURE TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
177 | TT-FA1076 | TT | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE (A) TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
178 | TT-FA1077 | TT | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE (B) TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
212 | TW-FA1077 | TW | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-052 | -340~2500 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
208 | TE-FA1077 | TE | FA1077 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-052 | -340~2500 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
211 | TW-FA1076 | TW | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
207 | TE-FA1076 | TE | FA1076 | #1 PRIMARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-052 | -340~2500 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
20 | FE-FA1079 | FE | FA1079 | #1 PRIMARY AIR SYSTEM FLOW ELEMENT | PD-052 | -340~2500 mmH2O | 343 | 0~510 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
22 | FT-FA1079 | FT | FA1079 | #1 PRIMARY AIR SYSTEM FLOW TRANSMITTER | PD-052 | -340~2500 mmH2O | 343 | 0~510 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
27 | DPG-FG1052-4 | DPG | FG1052-4 | #1 PRIMARY AIR/GAS COLD END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
25 | DPG-FG1052-2 | DPG | FG1052-2 | #1 PRIMARY AIR/GAS HOT END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
8 | PT-HR1003-1 | PT | HR1003-1 | #1 REHEAT STEAM PRESSURE TRANSMITTER-1 | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
9 | PT-HR1003-2 | PT | HR1003-2 | #1 REHEAT STEAM PRESSURE TRANSMITTER-2 | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
24 | TW-HR1004 | TW | HR1004 | #1 REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
21 | TE-HR1004 | TE | HR1004 | #1 REHEAT STEAM TEMPERATURE ELEMENT | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
11 | TT-HR1004 | TT | HR1004 | #1 REHEAT STEAM TEMPERATURE TRANSMITTER | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
20 | TW-CR1005-1 | TW | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
17 | TE-CR1005-1 | TE | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
21 | TW-CR1005-2 | TW | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 395 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
18 | TE-CR1005-2 | TE | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 395 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
7 | TT-CR1005-1 | TT | CR1005-1 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
8 | TT-CR1005-2 | TT | CR1005-2 | #1 REHEATER DESUPERHEATER OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 45 | 395 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
6 | PT-CR1006 | PT | CR1006 | #1 REHEATER HEADER PRESSURE TRANSMITTER | PD-012 | 45 | 395 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
21 | VT-FW1115-B31 | VT | FW1115-B31 | #1 BFP(B) MOTOR CASING (DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
22 | VT-FW1115-B32 | VT | FW1115-B32 | #1 BFP(B) MOTOR CASING (DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
23 | VT-FW1115-B41 | VT | FW1115-B41 | #1 BFP(B) MOTOR CASING (NON-DRIVEN END) X DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
24 | VT-FW1115-B42 | VT | FW1115-B42 | #1 BFP(B) MOTOR CASING (NON-DRIVEN END) Y DIRECTION VIBRATION TRANSMITTER | PD-017 | - | - | 0~25.4 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (BFP) |  | 0 |  | VT
17 | XV-FW1061 | XV | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 100 | 180 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
18 | XV-FW1111-1 | XV | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
19 | XV-FW1111-2 | XV | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
20 | XV-FW1121-1 | XV | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
21 | XV-FW1121-2 | XV | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP | PD-017 | 230 | 275 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
22 | XV-FW1151 | XV | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE | PD-017 | 100 | 180 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
7 | PT-HR1001 | PT | HR1001 | #1 REHEATER OUTLET HEADER PRESSURE TRANSMITTER | PD-012 | 45 | 550 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
22 | TW-HR1002-1 | TW | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
19 | TE-HR1002-1 | TE | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-1 | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
23 | TW-HR1002-2 | TW | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 550 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
20 | TE-HR1002-2 | TE | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE ELEMENT-2 | PD-012 | 45 | 550 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
9 | TT-HR1002-1 | TT | HR1002-1 | #1 REHEATER OUTLET TEMPERATURE TRANSMITTER-1 | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
10 | TT-HR1002-2 | TT | HR1002-2 | #1 REHEATER OUTLET TEMPERATURE TRANSMITTER-2 | PD-012 | 45 | 550 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
190 | TW-FG1100 | TW | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
186 | TE-FG1100 | TE | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 900 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
149 | TT-FG1100 | TT | FG1100 | #1 REHEATER-1 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 900 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
192 | TW-FG1102 | TW | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
188 | TE-FG1102 | TE | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 700 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
151 | TT-FG1102 | TT | FG1102 | #1 REHEATER-2 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 700 | 0~900 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
194 | TW-FG1104 | TW | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 600 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
190 | TE-FG1104 | TE | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 600 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
153 | TT-FG1104 | TT | FG1104 | #1 REHEATER-3 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 600 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
196 | TW-FG1106 | TW | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
192 | TE-FG1106 | TE | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 520 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
155 | TT-FG1106 | TT | FG1106 | #1 REHEATER-4 INLET FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | ±890 mmH2O | 520 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
120 | PG-CW1140-5 | PG | CW1140-5 | #1 SAMPLING SYSTEM CHILLER UNIT COOLING WATER SUPPLY PRESSURE GAUGE DOWNSTREAM Y-STRAINER | PD-044 | 0.5 | 30 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
119 | PG-CW1140-4 | PG | CW1140-4 | #1 SAMPLING SYSTEM CHILLER UNIT COOLING WATER SUPPLY PRESSURE GAUGE UPSTREAM Y-STRAINER | PD-044 | 0.5 | 30 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
1 | FG-CW1140-6 | FG | CW1140-6 | #1 SAMPLING SYSTEM CHILLER UNIT WATER FLOWMETER | PD-044 | - | - | 1~10L/H | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
2 | FG-CW1140-7 | FG | CW1140-7 | #1 SAMPLING SYSTEM COOLING WATER RETURN LINE FLOWMETER | PD-044 | 5 | 40 | 2.5~25L/H | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
118 | PG-CW1140-2 | PG | CW1140-2 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY PRESSURE GAUGE DOWWNSTREAM Y-STRAINER | PD-044 | 5 | 40 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
117 | PG-CW1140-1 | PG | CW1140-1 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY PRESSURE GAUGE UPSTREAM Y-STRAINER | PD-044 | 5 | 40 | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
86 | TG-CW1140-3 | TG | CW1140-3 | #1 SAMPLING SYSTEM COOLING WATER SUPPLY THERMOMETER | PD-044 | 5 | 40 | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
16 | FG-SP1014 | FG | SP1014 | #1 SATURATED STEAM FLOWMETER FOR CONDUCTIVITY SENSOR | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
17 | FG-SP1015 | FG | SP1015 | #1 SATURATED STEAM FLOWMETER FOR SILICA ANALYZER | PD-044 | 100PSI | 65 | 300mL/min | - | - | - | - | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | FG
126 | PG-SP1006 | PG | SP1006 | #1 SATURATED STEAM PRESSUE GAUGE | PD-044 | - | - | - | - | - | - | BOURDON | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | PG
15 | AT-SP1015 | AT | SP1015 | #1 SATURATED STEAM SILICA | PD-044 | 148 | 343 | 0~100ppb | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
14 | AT-SP1014 | AT | SP1014 | #1 SATURATED STEAM SPECIFIC CONDUCTIVITY | PD-044 | 148 | 343 | 0~100 μs/cm | WET AI 4~20mA | SAMPLING RACK | DCS | - | PACKAGE (SAMPLING ) |  | 0 |  | AT
92 | TG-SP1006 | TG | SP1006 | #1 SATURATED STEAM THERMOMETER | PD-044 | - | - | 0~100 | - | - | - | BI-METAL | PACKAGE (SAMPLING) | NEW ADDED | 0 |  | TG
73 | PG-SW1503-A2 | PG | SW1503-A2 | #1 SEAWATER BOOSTER PUMP A DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
72 | PG-SW1503-A1 | PG | SW1503-A1 | #1 SEAWATER BOOSTER PUMP A SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
129 | TW-SW1503-A | TW | SW1503-A | #1 SEAWATER BOOSTER PUMP A SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
54 | TG-SW1503-A | TG | SW1503-A | #1 SEAWATER BOOSTER PUMP A SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
75 | PG-SW1503-B2 | PG | SW1503-B2 | #1 SEAWATER BOOSTER PUMP B DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
74 | PG-SW1503-B1 | PG | SW1503-B1 | #1 SEAWATER BOOSTER PUMP B SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
130 | TW-SW1503-B | TW | SW1503-B | #1 SEAWATER BOOSTER PUMP B SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
55 | TG-SW1503-B | TG | SW1503-B | #1 SEAWATER BOOSTER PUMP B SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
77 | PG-SW1503-C2 | PG | SW1503-C2 | #1 SEAWATER BOOSTER PUMP C DISCHARGE PRESSURE GAUGE | PD-020 | 7 | 50 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
76 | PG-SW1503-C1 | PG | SW1503-C1 | #1 SEAWATER BOOSTER PUMP C SUCTION PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
131 | TW-SW1503-C | TW | SW1503-C | #1 SEAWATER BOOSTER PUMP C SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
56 | TG-SW1503-C | TG | SW1503-C | #1 SEAWATER BOOSTER PUMP C SUCTION TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
69 | PG-SW1501-A | PG | SW1501-A | #1 SEAWATER PUMP (A) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
111 | TE-SW1501-A31 | TE | SW1501-A31 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
112 | TE-SW1501-A32 | TE | SW1501-A32 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
88 | TT-SW1501-A3 | TT | SW1501-A3 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
113 | TE-SW1501-A41 | TE | SW1501-A41 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
114 | TE-SW1501-A42 | TE | SW1501-A42 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
89 | TT-SW1501-A4 | TT | SW1501-A4 | #1 SEAWATER PUMP (A) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
115 | TE-SW1501-AU1 | TE | SW1501-AU1 | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
116 | TE-SW1501-AU2 | TE | SW1501-AU2 | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
90 | TT-SW1501-AU | TT | SW1501-AU | #1 SEAWATER PUMP (A) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
117 | TE-SW1501-AV1 | TE | SW1501-AV1 | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
118 | TE-SW1501-AV2 | TE | SW1501-AV2 | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
91 | TT-SW1501-AV | TT | SW1501-AV | #1 SEAWATER PUMP (A) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
119 | TE-SW1501-AW1 | TE | SW1501-AW1 | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
120 | TE-SW1501-AW2 | TE | SW1501-AW2 | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
92 | TT-SW1501-AW | TT | SW1501-AW | #1 SEAWATER PUMP (A) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
70 | PG-SW1501-B | PG | SW1501-B | #1 SEAWATER PUMP (B) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
93 | TT-SW1501-B3 | TT | SW1501-B3 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
94 | TT-SW1501-B4 | TT | SW1501-B4 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
121 | TE-SW1501-B31 | TE | SW1501-B31 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
122 | TE-SW1501-B32 | TE | SW1501-B32 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
123 | TE-SW1501-B41 | TE | SW1501-B41 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
124 | TE-SW1501-B42 | TE | SW1501-B42 | #1 SEAWATER PUMP (B) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
125 | TE-SW1501-BU1 | TE | SW1501-BU1 | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
126 | TE-SW1501-BU2 | TE | SW1501-BU2 | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
95 | TT-SW1501-BU | TT | SW1501-BU | #1 SEAWATER PUMP (B) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
127 | TE-SW1501-BV1 | TE | SW1501-BV1 | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
128 | TE-SW1501-BV2 | TE | SW1501-BV2 | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
96 | TT-SW1501-BV | TT | SW1501-BV | #1 SEAWATER PUMP (B) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
129 | TE-SW1501-BW1 | TE | SW1501-BW1 | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
130 | TE-SW1501-BW2 | TE | SW1501-BW2 | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
97 | TT-SW1501-BW | TT | SW1501-BW | #1 SEAWATER PUMP (B) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
71 | PG-SW1501-C | PG | SW1501-C | #1 SEAWATER PUMP (C) DISCHARGE PRESSURE GAUGE | PD-020 | 5 | 50 | 0~5 | - | - | - | BOURDON | FHI |  | 0 |  | PG
131 | TE-SW1501-C31 | TE | SW1501-C31 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
132 | TE-SW1501-C32 | TE | SW1501-C32 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
98 | TT-SW1501-C3 | TT | SW1501-C3 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
133 | TE-SW1501-C41 | TE | SW1501-C41 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
134 | TE-SW1501-C42 | TE | SW1501-C42 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
99 | TT-SW1501-C4 | TT | SW1501-C4 | #1 SEAWATER PUMP (C) MOTOR SIDE BEARING NON-DRIVEN END TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
135 | TE-SW1501-CU1 | TE | SW1501-CU1 | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
136 | TE-SW1501-CU2 | TE | SW1501-CU2 | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
100 | TT-SW1501-CU | TT | SW1501-CU | #1 SEAWATER PUMP (C) MOTOR WINDING (U) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
137 | TE-SW1501-CV1 | TE | SW1501-CV1 | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
138 | TE-SW1501-CV2 | TE | SW1501-CV2 | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
101 | TT-SW1501-CV | TT | SW1501-CV | #1 SEAWATER PUMP (C) MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
139 | TE-SW1501-CW1 | TE | SW1501-CW1 | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
140 | TE-SW1501-CW2 | TE | SW1501-CW2 | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-020 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SEAWTER PUMP) |  | 0 |  | TE
102 | TT-SW1501-CW | TT | SW1501-CW | #1 SEAWATER PUMP (C) MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-020 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
132 | TW-SW1551 | TW | SW1551 | #1 SEAWATER PUMP DISCHARGE HEADER TEMPERATURE GAUGE | PD-020 | 5 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
57 | TG-SW1551 | TG | SW1551 | #1 SEAWATER PUMP DISCHARGE HEADER TEMPERATURE GAUGE | PD-020 | 5 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
18 | LT-SW1501 | LT | SW1501 | #1 SEAWATER PUMP INLET LEVEL TRANSMITTER | PD-020 | 1 | 65 | 0.5~15M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
24 | TE-FA1054-1 | TE | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
179 | TT-FA1054-1 | TT | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
57 | VT-FA1054-1 | VT | FA1054-1 | #1 SECONDARY AIR FAN EXPANSION BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
21 | FE-FA1081 | FE | FA1081 | #1 SECONDARY AIR FAN INLET AIR FLOW ELEMENT | PD-053 | 0 | 66 | - | - | - | - | VENTURI | PACKAGE (SAF) |  | 0 |  | FE
23 | FT-FA1081 | FT | FA1081 | #1 SECONDARY AIR FAN INLET AIR FLOW TRANSMITTER | PD-053 | 0 | 66 | 0~432 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
213 | TW-FA1082 | TW | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-053 | 0 | 66 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
209 | TE-FA1082 | TE | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE ELEMENT | PD-053 | 0 | 66 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
186 | TT-FA1082 | TT | FA1082 | #1 SECONDARY AIR FAN INLET AIR TEMPERATURE TRANSMITTER TRANSMITTER | PD-053 | 0 | 66 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
83 | ZSC-FA1054-1 | ZSC | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
106 | ZSO-FA1054-1 | ZSO | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
56 | TS-FA1054-1 | TS | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-053 | - | - | - | DI | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
23 | MCV-FA1054-1 | MCV | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV | PD-053 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
129 | ZT-FA1054-1 | ZT | FA1054-1 | #1 SECONDARY AIR FAN INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-053 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
27 | TE-FA1054-4 | TE | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
182 | TT-FA1054-4 | TT | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
60 | VT-FA1054-4 | VT | FA1054-4 | #1 SECONDARY AIR FAN MOTOR BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
26 | TE-FA1054-3 | TE | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SFAFT SIDE BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
59 | VT-FA1054-3 | VT | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SFAFT SIDE BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
181 | TT-FA1054-3 | TT | FA1054-3 | #1 SECONDARY AIR FAN MOTOR SHAFT SIDE BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
28 | TE-FA1054-U1 | TE | FA1054-U1 | #1 SECONDARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
29 | TE-FA1054-U2 | TE | FA1054-U2 | #1 SECONDARY AIR FAN MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
30 | TE-FA1054-V1 | TE | FA1054-V1 | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
31 | TE-FA1054-V2 | TE | FA1054-V2 | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
184 | TT-FA1054-V | TT | FA1054-V | #1 SECONDARY AIR FAN MOTOR WINDING (V) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
32 | TE-FA1054-W1 | TE | FA1054-W1 | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
33 | TE-FA1054-W2 | TE | FA1054-W2 | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE ELEMENT-2 | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
185 | TT-FA1054-W | TT | FA1054-W | #1 SECONDARY AIR FAN MOTOR WINDING (W) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
183 | TT-FA1054-U | TT | FA1054-U | #1 SECONDARY AIR FAN MOTOR WINRING (U) TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
25 | TE-FA1054-2 | TE | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING TEMPERATURE | PD-053 | - | - | - | - | FIELD | TT | RTD | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
180 | TT-FA1054-2 | TT | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING TEMPERATURE TRANSMITTER | PD-053 | - | - | 0~200 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
58 | VT-FA1054-2 | VT | FA1054-2 | #1 SECONDARY AIR FAN NON-EXPANSION BEARING VIBRATION TRANSMITTER | PD-053 | - | - | 0~20mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SAF) |  | 0 |  | SECONDARY AIR FAN
71 | PT-FA1085 | PT | FA1085 | #1 SECONDARY AIR PREHEATER INLET AIR PRESSURE TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
187 | TT-FA1083 | TT | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE (A) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
188 | TT-FA1084 | TT | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE (B) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 80 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
214 | TW-FA1083 | TW | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
210 | TE-FA1083 | TE | FA1083 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
215 | TW-FA1084 | TW | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
211 | TE-FA1084 | TE | FA1084 | #1 SECONDARY AIR PREHEATER INLET AIR TEMPERATURE ELEMENT(B) | PD-053 | -3.3~2000 mmH2O | 80 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
72 | PT-FA1088 | PT | FA1088 | #1 SECONDARY AIR PREHEATER OUTLET AIR PRESSURE TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~3000 mmH2O | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | PT
189 | TT-FA1086 | TT | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE (A) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
190 | TT-FA1087 | TT | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE (B) TRANSMITTER | PD-053 | -3.3~2000 mmH2O | 343 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
217 | TW-FA1087 | TW | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
213 | TE-FA1087 | TE | FA1087 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT (B) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
216 | TW-FA1086 | TW | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
212 | TE-FA1086 | TE | FA1086 | #1 SECONDARY AIR PREHEATER OUTLET AIR TEMPERATURE ELEMENT(A) | PD-053 | -3.3~2000 mmH2O | 343 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
26 | DPG-FG1052-3 | DPG | FG1052-3 | #1 SECONDARY AIR/GAS COLD END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
24 | DPG-FG1052-1 | DPG | FG1052-1 | #1 SECONDARY AIR/GAS HOT END DIFFERENTIAL PRESSURE INDICATOR |  | - | - | 0~0.33Kg/cm² | - | - | - | - | PACKAGE (AIR PRE HEATER) |  | 1 |  | AIR PREHEATER
25 | VT-SW1501-A1 | VT | SW1501-A1 | #1 SEWATER PUMP (A) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
26 | VT-SW1501-A2 | VT | SW1501-A2 | #1 SEWATER PUMP (A) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
27 | VT-SW1501-B1 | VT | SW1501-B1 | #1 SEWATER PUMP (B) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
28 | VT-SW1501-B2 | VT | SW1501-B2 | #1 SEWATER PUMP (B) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
29 | VT-SW1501-C1 | VT | SW1501-C1 | #1 SEWATER PUMP (C) DISCHARGE ELBOW VIBRATION TRANSMITTER-1 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
30 | VT-SW1501-C2 | VT | SW1501-C2 | #1 SEWATER PUMP (C) DISCHARGE ELBOW VIBRATION TRANSMITTER-2 | PD-020 | - | - | 0~25 mm/s | AI 4~20mA | FIELD | DCS | - | PACKAGE (SEWATER PUMP) |  | 0 |  | VT
8 | XV-SB1054 | XV | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE | PD-015 | 30 | 360 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
9 | XV-SB1059 | XV | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE | PD-015 | 30 | 360 | - | DO | DCS | FIELD | ON/OFF | FHI |  | 0 |  | XV
102 | ZSC-SB1054 | ZSC | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
104 | ZSC-SB1059 | ZSC | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
103 | ZSO-SB1054 | ZSO | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
105 | ZSO-SB1059 | ZSO | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
10 | SV-SB1054 | SV | SB1054 | #1 SOOT BLOWING STEAM DRAIN VALVE SOLENOID VALVE | PD-015 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
11 | SV-SB1059 | SV | SB1059 | #1 SOOT BLOWING STEAM DRAIN VALVE SOLENOID VALVE | PD-015 | - | - | - | - | - | - | DC24V | FHI |  | 0 |  | SV
35 | ZT-SB1053 | ZT | SB1053 | #1 SOOT BLOWING STEAM PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-015 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
27 | MV-SB1001 | MV | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV | PD-015 | 153.5 | 440 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
99 | ZSC-SB1001 | ZSC | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV CLOSE POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
100 | ZSO-SB1001 | ZSO | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV OPEN POSITION SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
34 | ZT-SB1001 | ZT | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV POSITION TRANSMITTER | PD-015 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
101 | TS-SB1001 | TS | SB1001 | #1 SOOT BLOWING STEAM SHUT-OFF MOV TORQUE SWITCH | PD-015 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
10 | PG-SB1051 | PG | SB1051 | #1 SOOTBLOWING HEADER STEAM PRESSURE GAUGE | PD-015 | 30 | 360 | 0~50 | - | - | - | BOURDON | FHI |  | 0 |  | PG
17 | PT-SB1052 | PT | SB1052 | #1 SOOTBLOWING HEADER STEAM PRESSURE TRANSMITTER | PD-015 | 30 | 360 | 0~50 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
54 | TW-SB1056 | TW | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
33 | TE-SB1056 | TE | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
53 | TW-SB1055 | TW | SB1055 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
11 | TG-SB1055 | TG | SB1055 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
22 | TT-SB1056 | TT | SB1056 | #1 SOOTBLOWING LINE A STEAM TEMPERATURE TRANSMITTER | PD-015 | 30 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
55 | TW-SB1057 | TW | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
34 | TE-SB1057 | TE | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE ELEMENT | PD-015 | 30 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
56 | TW-SB1058 | TW | SB1058 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
12 | TG-SB1058 | TG | SB1058 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE GAUGE | PD-015 | 30 | 360 | 0~500 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
23 | TT-SB1057 | TT | SB1057 | #1 SOOTBLOWING LINE B STEAM TEMPERATURE TRANSMITTER | PD-015 | 30 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
8 | PCV-SB1053 | PCV | SB1053 | #1 SOOTBLOWING STEAM PRESSURE CONTROL VALVE | PD-015 | 153.5 | 440 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
24 | AT-FG1057-3 | AT | FG1057-3 | #1 STACK FLUE GAS CO ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
26 | AT-FG1057-5 | AT | FG1057-5 | #1 STACK FLUE GAS DUST ANALYZER | PD-051 | ±410mmAq | 200 | 0~1000 mg/m3 | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
20 | FT-FG1057-7 | FT | FG1057-7 | #1 STACK FLUE GAS FLOW TRANSMITTER | PD-051 | 33 mmH2O | 200 | 0~886.6 | WET AI 4~20mA | FIELD | DCS | ULTRASONIC | PACKAGE (CEMS) |  | 0 |  | FT
23 | AT-FG1057-2 | AT | FG1057-2 | #1 STACK FLUE GAS NOX ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
25 | AT-FG1057-4 | AT | FG1057-4 | #1 STACK FLUE GAS O2 ANALYZER | PD-051 | ±410mmAq | 200 | 0~21% | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
27 | AT-FG1057-6 | AT | FG1057-6 | #1 STACK FLUE GAS OPACITY ANALYZER | PD-051 | ±410mmAq | 200 | 0~100% | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
22 | AT-FG1057-1 | AT | FG1057-1 | #1 STACK FLUE GAS SOX ANALYZER | PD-051 | ±410mmAq | 200 | 0~1500ppm | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | AT
165 | TW-FG1057-8 | TW | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | - | - | - | PACKAGE (CEMS) | NEW ADDED | 0 |  | TW
161 | TE-FG1057-8 | TE | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE ELEMENT | PD-051 | ±890mmH2O | 200 | - | - | FIELD | TT | - | PACKAGE (CEMS) |  | 0 |  | TE
124 | TT-FG1057-8 | TT | FG1057-8 | #1 STACK FLUE GAS TEMPERATURE TRANSMITTER | PD-051 | 33 mmH2O | 200 | 0~300 | WET AI 4~20mA | CEMS | DCS | - | PACKAGE (CEMS) |  | 0 |  | TT
5 | MCV-FA1043-A | MCV | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,2/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
33 | ZSC-FA1043-A | ZSC | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
40 | ZSO-FA1043-A | ZSO | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
46 | ZT-FA1043-A | ZT | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,2/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
23 | TS-FA1043-A | TS | FA1043-A | #1 START UP BURNER A HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
51 | MCV-FA1043-B | MCV | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,3/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
79 | ZSC-FA1043-B | ZSC | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
86 | ZSO-FA1043-B | ZSO | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
92 | ZT-FA1043-B | ZT | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,3/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
69 | TS-FA1043-B | TS | FA1043-B | #1 START UP BURNER B HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
97 | MCV-FA1043-C | MCV | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,4/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
125 | ZSC-FA1043-C | ZSC | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
132 | ZSO-FA1043-C | ZSO | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
138 | ZT-FA1043-C | ZT | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,4/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
115 | TS-FA1043-C | TS | FA1043-C | #1 START UP BURNER C HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
143 | MCV-FA1043-D | MCV | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV | PD-022,5/5 | - | - | 0~100% | AO 4~20mA | DCS | FIELD | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
171 | ZSC-FA1043-D | ZSC | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV CLOSE POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
178 | ZSO-FA1043-D | ZSO | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
184 | ZT-FA1043-D | ZT | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV POSITION TRANSMITTER | PD-022,5/5 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
161 | TS-FA1043-D | TS | FA1043-D | #1 START UP BURNER D HOT SECONDARY AIR INLET CONTROL DAMPER MOV TORQUE SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 1 |  | DIESEL OIL AND BURNER
15 | FE-FA1043-A | FE | FA1043-A | #1 START-UP BURNER(A) HOT SECONDARY AIR FLOW ELEMENT | PD-022,2/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
16 | FT-FA1043-A | FT | FA1043-A | #1 START-UP BURNER(A) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,2/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
16 | FE-FA1043-B | FE | FA1043-B | #1 START-UP BURNER(B) HOT SECONDARY AIR FLOW ELEMENT | PD-022,3/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
17 | FT-FA1043-B | FT | FA1043-B | #1 START-UP BURNER(B) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,3/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
17 | FE-FA1043-C | FE | FA1043-C | #1 START-UP BURNER(C) HOT SECONDARY AIR FLOW ELEMENT | PD-022,4/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
18 | FT-FA1043-C | FT | FA1043-C | #1 START-UP BURNER(C) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,4/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
18 | FE-FA1043-D | FE | FA1043-D | #1 START-UP BURNER(D) HOT SECONDARY AIR FLOW ELEMENT | PD-022,5/5 | -3.3~2000 mmH2O | 343 | 0~65 | - | - | - | PITOT TUBE | FHI |  | 0 |  | FE
19 | FT-FA1043-D | FT | FA1043-D | #1 START-UP BURNER(D) HOT SECONDARY AIR FLOW TRANSMITTER | PD-022,5/5 | -3.3~2000 mmH2O | 343 | 0~65 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | FT
25 | MV-AS1395 | MV | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
93 | ZSC-AS1395 | ZSC | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
94 | ZSO-AS1395 | ZSO | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
32 | ZT-AS1395 | ZT | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
95 | TS-AS1395 | TS | AS1395 | #1 START-UP EJECTOR STEAM INLET SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
9 | TG-CD1119-1 | TG | CD1119-1 | #1 STEAM JET AIR EJECTOR CONDENSER COOLING WATER INLET TEMPERATURE GAUGE | PD-014 | - | 44 | 0~100 | - | - | - | - | PACKAGE (AIR EJECTOR) | NEW ADDED | 0 |  | TG
10 | TG-CD1119-2 | TG | CD1119-2 | #1 STEAM JET AIR EJECTOR CONDENSER COOLING WATER OUTLET TEMPERATURE GAUGE | PD-014 | - | 49.5 | 0~100 | - | - | - | - | PACKAGE (AIR EJECTOR) | NEW ADDED | 0 |  | TG
72 | TW-CD1119 | TW | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
63 | TE-CD1119 | TE | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE ELEMENT | PD-016 | 24 | 65 | - | - | FIELD | TT | RTD | FHI |  | 0 |  | TE
73 | TW-CD1119(G) | TW | CD1119(G) | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
18 | TG-CD1119 | TG | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE GAUGE | PD-016 | 24 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
46 | TT-CD1119 | TT | CD1119 | #1 STEAM JET AIR EJECTOR CONDENSER OUTLET WATER TEMPERATURE TRANSMITTER | PD-016 | 24 | 65 | 0~100 | AI 4~20mA | FIELD | DCS | SMART | FHI | RTD | 0 |  | TT
8 | PG-AS1013 | PG | AS1013 | #1 STEAM JET AIR EJECTOR CONDENSER PRESSURE GAUGE-1 | PD-014 | Full Vaccum & 0 | 350 | -1~0 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
9 | PG-AS1014 | PG | AS1014 | #1 STEAM JET AIR EJECTOR CONDENSER PRESSURE GAUGE-2 | PD-014 | 0.055Kg/c㎡A | 30.2 | -1~1 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
97 | ZSO-AS1396 | ZSO | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV OPEN POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
26 | MV-AS1396 | MV | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV | PD-014 | 13 | 390 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
96 | ZSC-AS1396 | ZSC | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV CLOSE POSITION SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
33 | ZT-AS1396 | ZT | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV POSITION TRANSMITTER | PD-014 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
98 | TS-AS1396 | TS | AS1396 | #1 STEAM JET AIR EJECTOR STEAM INLET SHUT-OFF MOV TORQUE SWITCH | PD-014 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
2 | PG-AS1006 | PG | AS1006 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE (START-UP) | PD-014 | 11 | 280 | 0~15 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
3 | PG-AS1007 | PG | AS1007 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-1 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
4 | PG-AS1008 | PG | AS1008 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-2 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
5 | PG-AS1009 | PG | AS1009 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-3 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
6 | PG-AS1011 | PG | AS1011 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-4 | PD-014 | 11 | 350 | 0~25 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
7 | PG-AS1012 | PG | AS1012 | #1 STEAM JET AIR EJECTOR STEAM PRESSURE GAUGE-5 | PD-014 | Full Vaccum & 0 | 350 | -1~0 | - | - | - | - | PACKAGE (AIR EJECTOR) |  | 0 |  | PG
143 | TW-CW1154-A1 | TW | CW1154-A1 | #1 STEAM TURBINE LUBE OIL COOLER A INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
66 | TG-CW1154-A1 | TG | CW1154-A1 | #1 STEAM TURBINE LUBE OIL COOLER A INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
144 | TW-CW1154-A2 | TW | CW1154-A2 | #1 STEAM TURBINE LUBE OIL COOLER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
67 | TG-CW1154-A2 | TG | CW1154-A2 | #1 STEAM TURBINE LUBE OIL COOLER A OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
145 | TW-CW1154-B1 | TW | CW1154-B1 | #1 STEAM TURBINE LUBE OIL COOLER B INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
68 | TG-CW1154-B1 | TG | CW1154-B1 | #1 STEAM TURBINE LUBE OIL COOLER B INLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
146 | TW-CW1154-B2 | TW | CW1154-B2 | #1 STEAM TURBINE LUBE OIL COOLER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
69 | TG-CW1154-B2 | TG | CW1154-B2 | #1 STEAM TURBINE LUBE OIL COOLER B OUTLET TEMPERATURE GAUGE | PD-021 | 10 | 65 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
35 | TCV-CW1201 | TCV | CW1201 | #1 STEAM TURBINE LUBE OIL TEMPERATURE CONTROL VALVE | PD-021 | 10 | 65 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
75 | ZT-CW1201 | ZT | CW1201 | #1 STEAM TURBINE LUBE OIL TEMPERATURE CONTROL VALVE POSITION TRANSMITTER | PD-021 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
40 | MV-BR1391 | MV | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV | PD-019 | 153.5 | 440 | - | DO | DCS | FIELD | DC TYPE | FHI |  | 0 |  | MV
180 | ZSC-BR1391 | ZSC | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV CLOSE POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
181 | ZSO-BR1391 | ZSO | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV OPEN POSITION SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
74 | ZT-BR1391 | ZT | BR1391 | #1 SUPERHEATER NO.1 OUTLET TO REHEATER SHUT-OFF MOV POSITION TRANSMITTER | PD-019 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
144 | ZSC-FW1001 | ZSC | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
147 | ZSC-FW1002 | ZSC | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
152 | ZSC-FW1060 | ZSC | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
154 | ZSC-FW1061 | ZSC | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
156 | ZSC-FW1111-1 | ZSC | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
158 | ZSC-FW1111-2 | ZSC | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
160 | ZSC-FW1121-1 | ZSC | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
162 | ZSC-FW1121-2 | ZSC | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUPCLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
164 | ZSC-FW1150 | ZSC | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
166 | ZSC-FW1151 | ZSC | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
168 | ZSC-FW1391 | ZSC | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
171 | ZSC-FW1392 | ZSC | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV CLOSE POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
145 | ZSO-FW1001 | ZSO | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
148 | ZSO-FW1002 | ZSO | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
150 | ZSO-FW1031 | ZSO | FW1031 | #1 BFP(A) SUCTION MANUAL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
151 | ZSO-FW1032 | ZSO | FW1032 | #1 BFP(B) SUCTION MANUAL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
153 | ZSO-FW1060 | ZSO | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
155 | ZSO-FW1061 | ZSO | FW1061 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
157 | ZSO-FW1111-1 | ZSO | FW1111-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
159 | ZSO-FW1111-2 | ZSO | FW1111-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUP OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
161 | ZSO-FW1121-1 | ZSO | FW1121-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
163 | ZSO-FW1121-2 | ZSO | FW1121-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER BLOCK VALVE-STARTUPOPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
165 | ZSO-FW1150 | ZSO | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
167 | ZSO-FW1151 | ZSO | FW1151 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER BLOCK VALVE OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
169 | ZSO-FW1391 | ZSO | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
172 | ZSO-FW1392 | ZSO | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV OPEN POSITION SWITCH | PD-017 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
50 | ZT-FW1001 | ZT | FW1001 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
51 | ZT-FW1002 | ZT | FW1002 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
107 | TW-BR1110 | TW | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 360 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
97 | TE-BR1110 | TE | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 360 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
74 | TT-BR1110 | TT | BR1110 | #1 SUPERHEATER PANEL NO.1 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 360 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
182 | TS-BR1391 | TS | BR1391 | #1 SUPERHEATER PANEL NO.1 INLET TO REHEATER MOV TORQUE SWITCH | PD-019 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
108 | TW-BR1120-1 | TW | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-1 | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
98 | TE-BR1120-1 | TE | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-1 | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
109 | TW-BR1120-2 | TW | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-2 | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
99 | TE-BR1120-2 | TE | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE ELEMENT-2 | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
75 | TT-BR1120-1 | TT | BR1120-1 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE TRANSMITTER-1 | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
76 | TT-BR1120-2 | TT | BR1120-2 | #1 SUPERHEATER PANEL NO.1 OUTLET STEAM TEMPERATURE TRANSMITTER-2 | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
28 | PT-BR1130 | PT | BR1130 | #1 SUPERHEATER PANEL NO.2 INLET STEAM PRESSURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~250 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
110 | TW-BR1130-1 | TW | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
111 | TW-BR1130-2 | TW | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
100 | TE-BR1130-1 | TE | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
101 | TE-BR1130-2 | TE | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 440 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
77 | TT-BR1130-1 | TT | BR1130-1 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
78 | TT-BR1130-2 | TT | BR1130-2 | #1 SUPERHEATER PANEL NO.2 INLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 440 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
112 | TW-BR1140-1 | TW | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
113 | TW-BR1140-2 | TW | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
102 | TE-BR1140-1 | TE | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
103 | TE-BR1140-2 | TE | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE ELEMENT | PD-019 | 153.5 | 521 | - | - | FIELD | TT | T/C | FHI |  | 0 |  | TE
79 | TT-BR1140-1 | TT | BR1140-1 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
80 | TT-BR1140-2 | TT | BR1140-2 | #1 SUPERHEATER PANEL NO.2 OUTLET STEAM TEMPERATURE TRANSMITTER | PD-019 | 153.5 | 521 | 0~600 | AI 4~20mA | FIELD | DCS | SMART | FHI |  | 0 |  | TT
46 | TW-TS1604 | TW | TS1604 | #1 TEST WELL AT EXTRACTION STEAM NO.2 LINE | PD-013 | 16 | 440 | - | - | - | - | - | FHI |  | 0 |  | TW
47 | TW-TS1606 | TW | TS1606 | #1 TEST WELL AT EXTRACTION STEAM NO.3 LINE | PD-013 | 6.2 | 380 | - | - | - | - | - | FHI |  | 0 |  | TW
52 | ZT-FW1060 | ZT | FW1060 | #1 HP TURBINE BYPASS DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
53 | ZT-FW1110-1 | ZT | FW1110-1 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
54 | ZT-FW1110-2 | ZT | FW1110-2 | #1 SUPERHEATER PANEL #1 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
55 | ZT-FW1120-1 | ZT | FW1120-1 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
1 | TW-CR1603 | TW | CR1603 | #1 TEST WELL AT COLD REHEAT LINE B | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
2 | TW-CR1605-1 | TW | CR1605-1 | #1 TEST WELL AT COLD REHEATER COMMON HEADER -1 | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
3 | TW-CR1605-2 | TW | CR1605-2 | #1 TEST WELL AT COLD REHEATER COMMON HEADER -2 | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
45 | TW-TS1602 | TW | TS1602 | #1 TEST WELL AT COLD REHEATER TO #2 HIGH PRESSURE HEATER | PD-013 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
77 | TW-CD1603 | TW | CD1603 | #1 TEST WELL AT CONDENSATE PUMP COMMON DISCHARGE | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0 |  | TW
80 | TW-CD1607 | TW | CD1607 | #1 TEST WELL AT DEAERATOR INLET CONDENSATE-1 | PD-016 | 24 | 200 | - | - | - | - | - | FHI |  | 0 |  | TW
81 | TW-CD1608 | TW | CD1608 | #1 TEST WELL AT DEAERATOR INLET CONDENSATE-2 | PD-016 | 24 | 200 | - | - | - | - | - | FHI |  | 0 |  | TW
78 | TW-CD1604 | TW | CD1604 | #1 TEST WELL AT GLAND STEAM CONDENSER OUTLET | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0 |  | TW
102 | TW-HD1601 | TW | HD1601 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.1 DRAIN LINE | PD-018 | 16 & Full Vaccum | 210 | - | - | - | - | - | FHI |  | 0 |  | TW
56 | ZT-FW1120-2 | ZT | FW1120-2 | #1 SUPERHEATER PANEL #2 OUTLET DESUPERHEATING SPRAY WATER CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
57 | ZT-FW1130-1 | ZT | FW1130-1 | #1 BOILER FEEDWATER FLOW CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
103 | TW-HD1602 | TW | HD1602 | #1 TEST WELL AT HIGH PRESSURE HEATER NO.2 DRAIN LINE | PD-018 | 45 & Full Vaccum | 260 | - | - | - | - | - | FHI |  | 0 |  | TW
58 | ZT-FW1130-2 | ZT | FW1130-2 | #1 BOILER FEEDWATER FLOW CONTROL VALVE-STARTUP POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
59 | ZT-FW1150 | ZT | FW1150 | #1 REHEATER INLET DESUPERHEATING SPRAY WATER CONTROL VALVE POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
28 | TW-HR1603-1 | TW | HR1603-1 | #1 TEST WELL AT HOT REHEATER COMMON -1 | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
29 | TW-HR1603-2 | TW | HR1603-2 | #1 TEST WELL AT HOT REHEATER COMMON -2 | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
14 | TW-MS1607 | TW | MS1607 | #1 TEST WELL AT HP TURBINE BYPASS OUTLET | PD-011 | 45 | 395 | - | - | - | - | - | FHI |  | 0 |  | TW
30 | TW-HR1605 | TW | HR1605 | #1 TEST WELL AT ILP TURBINE LEADING LINE A | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
31 | TW-HR1607 | TW | HR1607 | #1 TEST WELL AT ILP TURBINE LEADING LINE B | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
79 | TW-CD1605 | TW | CD1605 | #1 TEST WELL AT LOW PRESSURE HEATER NO.1 INLET CONDENSATE SIDE | PD-016 | 24 | 65 | - | - | - | - | - | FHI |  | 0 |  | TW
32 | TW-HR1608 | TW | HR1608 | #1 TEST WELL AT LP TURBINE BYPASS OUTLET | PD-012 | 15 | 280 | - | - | - | - | - | FHI |  | 0 |  | TW
10 | TW-MS1602-1 | TW | MS1602-1 | #1 TEST WELL AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
11 | TW-MS1602-2 | TW | MS1602-2 | #1 TEST WELL AT MAIN STEAM LINE-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
12 | TW-MS1604 | TW | MS1604 | #1 TEST WELL AT TURBINE LEADING LINE A | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
13 | TW-MS1606 | TW | MS1606 | #1 TEST WELL AT TURBINE LEADING LINE B | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
34 | TW-HR1902 | TW | HR1902 | #1 THERMOWELL WELL FOR TE-MS1902 AT ILP TURBINE LEADING LINE A | PD-012 | 45 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
15 | TW-MS1902-1 | TW | MS1902-1 | #1 THERMOWELL WELL FOR TE-MS1902-1 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
16 | TW-MS1902-2 | TW | MS1902-2 | #1 THERMOWELL WELL FOR TE-MS1902-2 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
17 | TW-MS1902-3 | TW | MS1902-3 | #1 THERMOWELL WELL FOR TE-MS1902-3 AT MAIN INLET STEAM LINE-1 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
18 | TW-MS1902-4 | TW | MS1902-4 | #1 THERMOWELL WELL FOR TE-MS1902-4 AT MAIN INLET STEAM LINE-2 | PD-011 | 144 | 550 | - | - | - | - | - | FHI |  | 0 |  | TW
33 | LS-WW1127 | LS | WW1127 | #1 TRANSFORMER AREA PIT A LEVEL SWITCH (LO-LO/LO/HI/HI-HI) | PD-040 | 0.25 | 45 |  | DI | FIELD | LCP | ELECTRODE | FHI |  | 0 |  | LS
36 | LSH-CH1101 | LSH | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL HIGH SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
35 | LSL-CH1101 | LSL | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
34 | LSLL-CH1101 | LSLL | CH1101 | #1 TRI-SODIUM PHOSPHATE SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-042 | - | - | - | DI | FIELD | DCS | - | PACKAGE (CHEMICAL DOSING) |  | 0 |  | LS
60 | ZT-FW1391 | ZT | FW1391 | #1 BFP(A) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
61 | ZT-FW1392 | ZT | FW1392 | #1 BFP(B) MAIN DISCHARGE SHUT-OFF VALVE BYPASS MOV POSITION TRANSMITTER | PD-017 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
1 | MV-AS1394 | MV | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV | PD-011 | 13 | 300 | - | DO | DCS | FIELD | - | FHI |  | 0 |  | MV
1 | ZSC-AS1394 | ZSC | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV CLOSE POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
2 | ZSO-AS1394 | ZSO | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV OPEN POSITION SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
1 | ZT-AS1394 | ZT | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV POSITION TRANSMITTER | PD-011 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
3 | TS-AS1394 | TS | AS1394 | #1 TURBINE WARMING VALVE INLET DRAIN MOV TORQUE SWITCH | PD-011 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
103 | PG-IW0809-A | PG | IW0809-A | ACTIVATED CARBON FILTER BACKWASH PUMP P-0809A DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
104 | PG-IW0809-B | PG | IW0809-B | ACTIVATED CARBON FILTER BACKWASH PUMP P-0809B DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
101 | PG-IW0808-A | PG | IW0808-A | ACTIVATED CARBON FILTER FEED PUMP P-0808A DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
102 | PG-IW0808-B | PG | IW0808-B | ACTIVATED CARBON FILTER FEED PUMP P-0808B DISCHARGE PRESSURE GAUGE | PD-025 | 7 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
38 | ZSO-DO1043-A1 | ZSO | DO1043-A1 | BURNER(A) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,2/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
84 | ZSO-DO1043-B1 | ZSO | DO1043-B1 | BURNER(B) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,3/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
130 | ZSO-DO1043-C1 | ZSO | DO1043-C1 | BURNER(C) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,4/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
176 | ZSO-DO1043-D1 | ZSO | DO1043-D1 | BURNER(D) FUEL OIL PNEUMATIC VALVE-1 OPEN POSITION SWITCH | PD-022,5/5 | - | - | - | DI | FIELD | DCS | - | PACKAGE (BURNER) |  | 0 |  | DIESEL OIL AND BURNER
19 | LG-MU0708-A | LG | MU0708-A | DEMINERALIZED WATER TANK A LEVEL GAUGE | PD-024 | 1.5 | 65 | 0~15 M | - | - | - | FLOAT | FHI |  | 0 |  | LG
26 | LS-MU0708-A | LS | MU0708-A | DEMINERALIZED WATER TANK A LEVEL LOW SWITCH | PD-024 | 1.5 | 65 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
21 | LT-MU0708-A | LT | MU0708-A | DEMINERALIZED WATER TANK A LEVEL TRANSMITTER | PD-024 | 1.5 | 65 | 0~15M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
20 | LG-MU0708-B | LG | MU0708-B | DEMINERALIZED WATER TANK B LEVEL GAUGE | PD-024 | 1.5 | 65 | 0~15 M | - | - | - | FLOAT | FHI |  | 0 |  | LG
27 | LS-MU0708-B | LS | MU0708-B | DEMINERALIZED WATER TANK B LEVEL LOW SWITCH | PD-024 | 1.5 | 65 | - | DI | FIELD | DCS | FLOAT | FHI |  | 0 |  | LS
22 | LT-MU0708-B | LT | MU0708-B | DEMINERALIZED WATER TANK B LEVEL TRANSMITTER | PD-024 | 1.5 | 65 | 0~15M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
11 | DPT-DO0001 | DPT | DO0001 | DIESEL OIL PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-022,1/5 | 7 | 70 | 0~1.0 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | DPT
84 | PG-DO0004 | PG | DO0004 | DIESEL OIL PUMP COMMON DISCHARGE PRESSURE GAUGE | PD-022,1/5 | 25 | 70 | 0~25 | - | - | - | BOURDON | FHI |  | 0 |  | PG
37 | PT-DO0005 | PT | DO0005 | DIESEL OIL PUMP COMMON DISCHARGE PRESSURE TRANSMITTER | PD-022,1/5 | 25 | 70 | 0~25 | AI 4~20mA | FIELD | DCS | CAPILLARY | FHI |  | 0 |  | PT
159 | TW-DO0003 | TW | DO0003 | DIESEL OIL PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
82 | TG-DO0003 | TG | DO0003 | DIESEL OIL PUMP COMMON DISCHARGE TEMPERATURE GAUGE | PD-022,1/5 | 25 | 70 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
37 | PCV-DO0002 | PCV | DO0002 | DIESEL OIL SYSTEM PRESSURE CONTROL VALVE | PD-022,1/5 | 18 | 70 | - | AO 4~20mA | DCS | FIELD | MODULATING | FHI |  | 0 |  | CV
76 | ZT-DO0002 | ZT | DO0002 | DIESEL OIL SYSTEM PRESSURE CONTROL VALVE POSITION TRANSMITTER | PD-022 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
3 | TE-P0719-3 | TE | P0719-3 | FIRE PUMP(A) MOTOR SIDE BEARING FRONT END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
4 | TE-P0719-4 | TE | P0719-4 | FIRE PUMP(A) MOTOR SIDE BEARING REAR END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
5 | TE-P0719-U1 | TE | P0719-U1 | FIRE PUMP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
6 | TE-P0719-U2 | TE | P0719-U2 | FIRE PUMP(A) MOTOR WINDING (U) TEMPERATURE ELEMENT-2 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
7 | TE-P0719-V1 | TE | P0719-V1 | FIRE PUMP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
8 | TE-P0719-V2 | TE | P0719-V2 | FIRE PUMP(A) MOTOR WINDING (V) TEMPERATURE ELEMENT-2 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
9 | TE-P0719-W1 | TE | P0719-W1 | FIRE PUMP(A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
10 | TE-P0719-W2 | TE | P0719-W2 | FIRE PUMP(A) MOTOR WINDING (W) TEMPERATURE ELEMENT-1 | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
1 | TE-P0719-1 | TE | P0719-1 | FIRE PUMP(A) PUMP SIDE BEARING FRONT END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
2 | TE-P0719-2 | TE | P0719-2 | FIRE PUMP(A) PUMP SIDE BEARING REAR END TEMPERATURE ELEMENT | - | - | - | - | - | FIELD | TT | RTD | PACKAGE (FIRE PUMP) |  | 0 |  | TE
26 | LG-IW0724-1 | LG | IW0724-1 | FIRE WATER TANK LEVEL GAUGE-1 | PD-025 | 1.5 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
27 | LG-IW0724-2 | LG | IW0724-2 | FIRE WATER TANK LEVEL GAUGE-2 | PD-025 | 1.5 | 65 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
28 | LG-IW0724-3 | LG | IW0724-3 | FIRE WATER TANK LEVEL GAUGE-3 | PD-025 | 1.5 | 65 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
29 | LG-IW0724-4 | LG | IW0724-4 | FIRE WATER TANK LEVEL GAUGE-4 | PD-025 | 1.5 | 65 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
30 | LG-IW0724-5 | LG | IW0724-5 | FIRE WATER TANK LEVEL GAUGE-5 | PD-025 | 1.5 | 65 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
29 | LS-IW0724 | LS | IW0724 | FIRE WATER TANK LEVEL LOW SWITCH | PD-025 | 1.5 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0 |  | LS
25 | LT-IW0724 | LT | IW0724 | FIRE WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~8.2 M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
4 | PG-0766 | PG | 0766 | HYPO-CHLORINATED DOSING PIPE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
5 | PG-0762A | PG | 0762A | HYPO-CHLORINATED DOSING SYSTEM NaOCL DOSING PUMP P-0762A DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
6 | PG-0762B | PG | 0762B | HYPO-CHLORINATED DOSING SYSTEM NaOCL DOSING PUMP P-0762B DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
1 | LG-0762A | LG | 0762A | HYPO-CHLORINATED DOSING SYSTEM TANK T-0762A LEVEL GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
2 | LG-0762B | LG | 0762B | HYPO-CHLORINATED DOSING SYSTEM TANK T-0762B LEVEL GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
3 | PG-0761 | PG | 0761 | HYPO-CHLORINATED DOSING SYSTEM TRANSFER PUMP P-0761 DISCHARGE PRESSURE GAUGE | PD-043 | - | - | - | - | - | - | - | PACKAGE (HYPO-CHLORINATED DOSING) | NEW ADDED | 1 |  | HYPO CHLORINATED DOSING
51 | LSH-CH0701 | LSH | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL HIGH SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0 |  | LS
50 | LSL-CH0701 | LSL | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL LOW SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0 |  | LS
49 | LSLL-CH0701 | LSLL | CH0701 | HYPO-CHLORINATED SOLUTION TANK LEVEL LOW-LOW SWITCH | PD-043 | - | - | - | DI | FIELD | DCS | - | PACKAGE (WATER PLANT) | DELETED | 0 |  | LS
162 | TW-IA0151 | TW | IA0151 | IA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-2/6 | 10 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
85 | TG-IA0151 | TG | IA0151 | IA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-2/6 | 10 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
107 | PG-IW0052 | PG | IW0052 | INDUSTRIAL WATER FOR WASTE WATER PUMP 0050A PRESSURE GAUGE | PD-040 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
108 | PG-IW0053 | PG | IW0053 | INDUSTRIAL WATER FOR WASTE WATER PUMP 0050B PRESSURE GAUGE | PD-040 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
99 | PG-IW0715-A | PG | IW0715-A | INDUSTRIAL WATER PUMP A DISCHARGE PRESSURE GAUGE | PD-025 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
15 | DPT-IW0715-A | DPT | IW0715-A | INDUSTRIAL WATER PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-025 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
100 | PG-IW0715-B | PG | IW0715-B | INDUSTRIAL WATER PUMP B DISCHARGE PRESSURE GAUGE | PD-025 | 10 | 65 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
16 | DPT-IW0715-B | DPT | IW0715-B | INDUSTRIAL WATER PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-025 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
55 | PT-IW0715 | PT | IW0715 | INDUSTRIAL WATER PUMP COMMON HEADER PRESSURE TRANSMITTER | PD-025 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
47 | MV-IW0391 | MV | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV | PD-025 | 1.5 | 65 | - | DO | DCS | FIELD |  | FHI | NEW ADDED | 0 |  | MV
203 | ZSC-IW0391 | ZSC | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV CLOSE POSITION SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
204 | ZSO-IW0391 | ZSO | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV OPEN POSITION SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
79 | ZT-IW0391 | ZT | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV POSITION TRANSMITTER | PD-025 | - | - | 0~100% | AI 4~20mA | FIELD | DCS | - | FHI |  | 0 |  | ZT
205 | TS-IW0391 | TS | IW0391 | INDUSTRIAL WATER TANK CONNECTING PIPE MOV TORQUE SWITCH | PD-025 | - | - | - | DI | FIELD | DCS | - | FHI |  | 0 |  | ZS
21 | LG-IW0714-1 | LG | IW0714-1 | INDUSTRIAL WATER TANK LEVEL GAUGE-1 | PD-025 | 1.5 | 65 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
22 | LG-IW0714-2 | LG | IW0714-2 | INDUSTRIAL WATER TANK LEVEL GAUGE-2 | PD-025 | 1.5 | 65 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
23 | LG-IW0714-3 | LG | IW0714-3 | INDUSTRIAL WATER TANK LEVEL GAUGE-3 | PD-025 | 1.5 | 65 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
24 | LG-IW0714-4 | LG | IW0714-4 | INDUSTRIAL WATER TANK LEVEL GAUGE-4 | PD-025 | 1.5 | 65 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
25 | LG-IW0714-5 | LG | IW0714-5 | INDUSTRIAL WATER TANK LEVEL GAUGE-5 | PD-025 | 1.5 | 65 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
28 | LS-IW0714 | LS | IW0714 | INDUSTRIAL WATER TANK LEVEL LOW SWITCH | PD-025 | 1.5 | 65 | - | DI | FIELD | DCS | MAGNETIC | FHI |  | 0 |  | LS
24 | LT-IW0714 | LT | IW0714 | INDUSTRIAL WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~8.2 M | WET AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
44 | PT-IA0107 | PT | IA0107 | INSTRUMENT AIR DRYER A OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
45 | PT-IA0127 | PT | IA0127 | INSTRUMENT AIR DRYER B OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
46 | PT-IA0147 | PT | IA0147 | INSTRUMENT AIR DRYER C OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
47 | PT-IA0706-A | PT | IA0706-A | INSTRUMENT AIR TANK A PRESSURE TRANSMITTER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
48 | PT-IA0706-B | PT | IA0706-B | INSTRUMENT AIR TANK B PRESSURE TRANSMITTER | PD-023,2/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
13 | PSL-IA1706 | PSL | IA1706 | INSTRUMENT AIR UNIT NO.1 PRESSURE LOW SWITCH | PD-023-5/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0 |  | PS
11 | PSL-IA1706-NC | PSL | IA1706-NC | INSTRUMENT AIR UNIT NO.1 PRESSURE NOT LOW SWITCH | PD-023,5/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0 |  | PS
51 | PT-IA1706 | PT | IA1706 | INSTRUMENT AIR UNIT NO.1 PRESSURE TRANSMITTER | PD-023,5/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
96 | PG-MU0709-A | PG | MU0709-A | MAKE-UP PUMP A DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
12 | DPT-MU0709-A | DPT | MU0709-A | MAKE-UP PUMP A SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
97 | PG-MU0709-B | PG | MU0709-B | MAKE-UP PUMP B DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
13 | DPT-MU0709-B | DPT | MU0709-B | MAKE-UP PUMP B SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
98 | PG-MU0709-C | PG | MU0709-C | MAKE-UP PUMP C DISCHARGE PRESSURE GAUGE | PD-024 | 10 | 30 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
14 | DPT-MU0709-C | DPT | MU0709-C | MAKE-UP PUMP C SUCTION STRAINER DIFFERENTIAL PRESSURE TRANSMITTER | PD-024 | 1.5 | 65 | 0~1 | AI 4~20mA | FIELD | DCS | DIFF. PRESS. | FHI |  | 0 |  | DPT
54 | PT-MU0709 | PT | MU0709 | MAKE-UP PUMP COMMON HEADER PRESSURE TRANSMITTER | PD-024 | 10 | 65 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
14 | LG-DO0701-1 | LG | DO0701-1 | OIL SERVICE TANK LEVEL GAUGE-1 | PD-022,1/5 | 1.5 | 70 | 0~2 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
15 | LG-DO0701-2 | LG | DO0701-2 | OIL SERVICE TANK LEVEL GAUGE-2 | PD-022,1/5 | 1.5 | 70 | 1.8~3.8 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
16 | LG-DO0701-3 | LG | DO0701-3 | OIL SERVICE TANK LEVEL GAUGE-3 | PD-022,1/5 | 1.5 | 70 | 3.6~5.6 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
17 | LG-DO0701-4 | LG | DO0701-4 | OIL SERVICE TANK LEVEL GAUGE-4 | PD-022,1/5 | 1.5 | 70 | 5.4~7.4 M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
18 | LG-DO0701-5 | LG | DO0701-5 | OIL SERVICE TANK LEVEL GAUGE-5 | PD-022,1/5 | 1.5 | 70 | 7.2~8.2M | - | - | - | MAGNETIC | FHI |  | 0 |  | LG
20 | LT-DO0701 | LT | DO0701 | OIL SERVICE TANK LEVEL TRANSMITTER | PD-022,1/5 | 1.5 | 70 | 0~8.2 M | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
39 | PT-PA0107 | PT | PA0107 | PA DRYER A OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
40 | PT-PA0127 | PT | PA0127 | PA DRYER B OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
41 | PT-PA0147 | PT | PA0147 | PA DRYER C OUTLET PRESSURE TRANSMITTER TO COMMON HEADER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
161 | TW-PA0151 | TW | PA0151 | PA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-1/6 | 10 | 50 | - | - | - | - | - | FHI | NEW ADDED | 0 |  | TW
84 | TG-PA0151 | TG | PA0151 | PA DRYER OUTLET COMMON HEADER TEMPERATURE GAUGE | PD-023-1/6 | 10 | 50 | 0~100 | - | - | - | BI-METAL | FHI |  | 0 |  | TG
42 | PT-PA0705-A | PT | PA0705-A | PLANT AIR TANK A PRESSURE TRANSMITTER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
43 | PT-PA0705-B | PT | PA0705-B | PLANT AIR TANK B PRESSURE TRANSMITTER | PD-023,1/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
12 | PSL-PA1705 | PSL | PA1705 | PLANT AIR TO UNIT NO.1 PRESSURE LOW SWITCH | PD-023-3/6 | 10 | 16 | 2.8 | DI | FIELD | IRP | BOURDON | FHI |  | 0 |  | PS
49 | PT-PA1705 | PT | PA1705 | PLANT AIR TO UNIT NO.1 PRESSURE TRANSMITTER | PD-023,3/6 | 10 | 60 | 0~10 | AI 4~20mA | FIELD | DCS | GAUGE PRESS. | FHI |  | 0 |  | PT
129 | PG-RW0862-A | PG | RW0862-A | RAW WATER FEED PUMP P-0862A DISCHARGE PRESSURE GAUGE | PD-045 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
130 | PG-RW0862-B | PG | RW0862-B | RAW WATER FEED PUMP P-0862B DISCHARGE PRESSURE GAUGE | PD-045 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
28 | LT-RW0717 | LT | RW0717 | RAW WATER PIT LEVEL TRANSMITTER | PD-045 | 1 | 45 | 0.5~5M | AI 4~20mA | FIELD | DCS | RADAR | FHI |  | 0 |  | LT
93 | PG-DW0858-A | PG | DW0858-A | REGENERATION WATER PUMP P-0858A DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
94 | PG-DW0858-B | PG | DW0858-B | REGENERATION WATER PUMP P-0858B DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
95 | PG-DW0858-C | PG | DW0858-C | REGENERATION WATER PUMP P-0858C DISCHARGE PRESSURE GAUGE | PD-024 | 3.5 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
23 | LT-IW0113 | LT | IW0113 | TURBINE BUILDING PLUMBING WATER TANK LEVEL TRANSMITTER | PD-025 | 1.5 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
28 | SV-IW0113 | SV | IW0113 | TURBINE BUILDING PLUMBING WATER TK INLET SOLENOID VALVE | PD-025 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
26 | LT-PW0114 | LT | PW0114 | TURBINE BUILDING POTABLE WATER TANK LEVEL TRANSMITTER | PD-026 | 3 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT
29 | SV-PW0114 | SV | PW0114 | TURBINE BUILDING POTABLE WATER TK INLET SOLENOID VALVE | PD-026 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
105 | PG-IW0895-A | PG | IW0895-A | UTILITY WATER PUMP P-0895A DISCHARGE PRESSURE GAUGE | PD-025 | 4 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
106 | PG-IW0895-B | PG | IW0895-B | UTILITY WATER PUMP P-0895B DISCHARGE PRESSURE GAUGE | PD-025 | 4 | 45 | 0~6 | - | - | - | BOURDON | FHI |  | 0 |  | PG
32 | LS-WW0058 | LS | WW0058 | WASTEWATER PIT T-0058 LEVEL SWITCH(HIGH-HIGH, HIGH, LOW, LOW-LOW) | PD-040 | 0.3 | 95 | - | DI | FIELD | LCP | ELECTRODE | FHI |  | 0 |  | LS
109 | PG-WW0058-A | PG | WW0058-A | WASTEWATER PUMP P-0058A DISCHARGE PRESSURE GAUGE | PD-040 | 7 | 90 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
110 | PG-WW0058-B | PG | WW0058-B | WASTEWATER PUMP P-0058B DISCHARGE PRESSURE GAUGE | PD-040 | 7 | 90 | 0~10 | - | - | - | BOURDON | FHI |  | 0 |  | PG
30 | SV-PW0721 | SV | PW0721 | WATER TREATMENT PLANT CONTROL BUILDING POTABLE WATER TANK INLET SOLENOID VALVE | PD-026 | 10 | 65 | - | DO | DCS | FIELD | DC24V | FHI |  | 0 |  | SV
27 | LT-PW0721 | LT | PW0721 | WATER TREATMENT PLANT CONTROL BUILDING POTABLE WATER TANK LEVEL TRANSMITTER | PD-026 | 3 | 65 | 0~2000 | AI 4~20mA | FIELD | DCS | DP(FLANGE MOUNTED) | FHI |  | 0 |  | LT