start-up procedure

| PR-ope-5002 |  |  |  |
| --- | --- | --- | --- |
| Prepared by: | R P. Del Mundo | Date Created: | 04-15-2017 |
| Reviewed by: | G T. Borja K R. Mendoza N L. Falcunit M P. Castro | Rev No. | 1 |
| Approved by: | Amatero Pete D. Ricablanca | Date Approved |  |

Document Revision Register Page

| Rev. No. | Description | Date Created | Date Approved | Author |
| --- | --- | --- | --- | --- |
| 00 | Initial Issue | 04-15-2017 | 08-01-2017 | EA Dela Cruz, JJM Lucio, KR Mendoza, APD Ricablanca |
| 01 | Procedure Update | 11-12-2019 |  | KR Mendoza / JS Legaspi |
| 02 | Format Update | 03-18-2024 |  | R P. Del Mundo |
|  | Change of company name and logo |  |  |  |
|  | Change of signatories |  |  |  |
| 03 | Procedure Update | 1/13/2025 |  | I Dinglasan |

1.0 PURPOSE AND SCOPE

## The procedures outlined here are intended to serve as guidelines for MANUAL and AUTOMATIC operation of the unit/plant.

## This procedure provides the initial conditions, precautions and the necessary instructions for the safe and orderly start up (Cold, Warm and Hot) of Boiler and Turbine/Generator of Reheater CFB Limay Power Plant.

- DEFINITIONS

  - Start-up applies to activities related to the start-up of the power plant from cold, warm, or hot conditions, establishment of steam and power generation with the generator synchronized to the grid and recovery restart from power plant trip.

  - Circulating Fluidized Bed (CFB) - the unit, balance-draft and circulating fluid bed boiler.

  - Cold Start-up – a condition considered when the temperature of the fluidized bed at the start-up burner elevation is below 700°C and a purge cycle must therefore include.

    - Ambient Cold – Prolonged Shut-Down

    - Cold Start 1 - >72 hrs

    - Cold Start 2 - >48hrs and ≤72 hrs

  - Warm Start-up – a condition considered when the temperature of the fluidized bed at the start-up burner elevation is below 700°C and a purge cycle must therefore include.

    - Warm Start - >8 hrs and ≤48 hrs shutdown

  - Hot Start-up – a condition where the boiler has been down for a comparatively short period of time and considerable drum pressure was maintained.

    - Hot Start up -  ≥8 hrs of shutdown

- ABBREVIATIONS

  - SUP – Start-up Procedure

  - IDF – Induced Draft Fan

  - PAF – Primary Air Fan

  - SAF – Secondary Air Fan

  - L – Local

  - DCS – Distributed Control System

  - PB – Push Button Switch

  - MOP – Main Oil Pump

  - COP – Control Oil Pump

  - EOP – Emergency Oil Pump

  - MSV – Main Stop Valve

  - MOV – Motor Operated Valve

  - ACWP – Auxiliary Cooling Water Pump

  - TCS – Turbine Control System

  - LCP – Local Control Panel

  - PCV – Pressure Control Valve

  - SSFV – Steam Seal Feed Valve

  - MSV – Main Stop Valve

  - CV – Control Valve

  - VV – Ventilator Valve

  - ICV – Intercept Valve

  - C/R – Cold Reheat

  - CRCV – Cold Reheat Check Valve

  - HPBV – High Pressure Bypass Valve

  - LPBV – Low Pressure Bypass Valve

  - ANN – Annunciator

- DETAILS

  - INITIAL CONDITIONS

    - Electrical line-up is completed and signed off.

    - Instrument valve line-ups are completed and Instrument valve line-up checklists are signed off.

    - System valve line-ups are completed and system valve line-up checklists are signed off.

    - Silos have been filled with enough inert, sorbent, liquid fuel and solid fuel materials.

    - All control systems have been checked out and are available for service. All safety interlocks are tested to properly functioning. Exercise the system by creating the actual interlock activating condition. Simulate the activating condition if the actual condition cannot be created.

    - All instrumentations have been checked out, calibrated and in-service.

    - All mechanical and auxiliary equipment and systems have been checked out and are available for service.

    - Lube Oil system of equipment is established.

    - The fuel firing equipment, coal and diesel oil has been checked out and available for service.

    - The limestone equipment has been checked out to assure proper functioning.

    - All air and gas handling equipment has been checked out and available for service. All air and gas duct dampers should be in startup position.

      - ID Fan inlet control valve closed.

      - PA Fan inlet control vanes open 25% or above.

      - SA Fan inlet control vanes open 25% or above.

      - Secondary air port dampers open.

      - Convective backpass flue gas biasing dampers on both superheat and reheat side specified open to ensure even heating of both parallel passes.

    - The soot blowing equipment has been checked for proper operation and the system is in the startup condition. All blowers retracted, main steam supply valves isolation open.

    - Ensure that the following systems are ready and/or in operation prior to boiler firing.

      - Power supply system is normal.

      - Instrument & Plant Air System is in operation wherein at least one (1) IA compressor and one (1) PA compressor are running.

      - Sea Water System and Close Cooling Water System are in operation.

      - Feed Water System is in operation.

      - Diesel Oil System is in operation and Fuel Oil circulation is established.

      - Electrostatic Precipitator Purge Air Fan and Heater is in operation.

      - Rotary Air Heater is in operation with Air Heater Sootblower (air) in continuous operation mode.

      - Sand Injection System is ready.

      - Limestone Injection System is ready.

      - Soot blowing System have been checked for proper operation and the system is in the start-up condition.

      - Coal Feeding System is ready.

    - Plant Personnel has successfully completed Boiler, Turbine and Generator Pre Start-up Check.

    - Shift Personnel receives advices and instructions from Operations Manager. He advises Maintenance Head for manpower coverage during start-up.  He conducts group discussions and review of the Start-up Procedures (SUP) giving emphasis on safety.

    - Personnel are assigned and designated to perform procedures, CFB Boiler, Turbine and Generator Start-up Preparation Up and ensure that checklists are completed.

  - PRECAUTIONS AND LIMITATIONS

    - No pending Permit to Work.

    - Firefighting system is ready and available.

    - Ensure areas are clean and in safe condition.

    - Start-up (Cold, Warm and Hot) shall follow the start-up curves.

    - The startup and step sequences of the burner is managed by the installed Distributive Control System (DCS).

    - All needed pressures of air and fuel, the positions of valves, dampers and the flame detection of main flame and ignition burner must be supervised by the control system in fail safe technology.

    - Before start-up of the burners, all manual valves have to be set in operation position, the automatic equipment has to be ready for operation.

    - For furnace purging, the damper has to be opened by the control system.

    - For the burner, there is an igniter for lighting the burner. It is useful to test the function of the igniter by separate signals “START IGNITOR” and “STOP IGNITOR”.  Testing of the igniter should only be possible if the furnace is purged and the main burner is not in operation.

    - Normally, the oil gun should be cleaned with purging air after a burner shutdown. Therefore, an appropriate program has to be provided in the control system.

    - If the igniter is in operation and all other operation conditions are fulfilled, the fuel shut off valves will open and the   ignition safety time and the burner stays in operation. If the flame detector sees the main flame, the igniter will switch off automatically.

    - Caution: The differential temperature between economizer water outlet temperature and drum metal temperature must never exceed 110oC to avoid thermal shocking of the drum.

    - Caution: The ID Fan is capable of developing a draft in excess of the furnace design pressure. Therefore, the operator must take care to establish and maintain an air flow path through the unit, prior to starting the I.D Fan and prior to opening the I.D. Fan inlet control vanes, by insuring that other dampers in the system are in the startup positions indicated above and all secondary air port dampers are open. I.D. Fan inlet control vanes should be kept closed until after the fan is started. This procedure will minimize the possibility of developing excessive negative pressure in the unit during the starting procedure.

    - Caution: Prevent possible water damage to the turbine by using extreme care to eliminate all water from the main steam line, cold and hot reheat lines, superheater and reheater elements and headers before the turbine is rolled.

    - When the turbine is operated, the operator must familiarize with symbols and functions blocks of the Turbine Control System(TCS) for plant operation methods, for safety and precautions.

    - Care must be exercised to prevent water from entering the main steam system line to the Turbine.

    - Main Control Room personnel had reviewed Turbine Start-up Diagram/Turbine Stop Diagram for precautions and limitations –Time Chart of Turbine Start-Up and Time Chart of Turbine Stop.

  - PROCEDURES

## START ESP (PURGE AIR HEATER, PURGE AIR FAN OF ELECTROSTATIC PRECIPITATOR)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| PURGE AIR HEATER/FAN, Rapping Hammer, Vibrator and Fly Ash Transmitters | H-1201/ F-1201 |  |  |  |  |  |  |  |  |  |
| - Ensure fan filter is clean. |  |  |  |  |  |  | √ |  |  |  |
| - Set MCC main power ON |  |  |  |  |  |  | √ |  |  |  |
| - Set Air circuit breaker ON |  |  |  |  |  |  | √ |  |  |  |
| - Check and initiate start of controlling at EP PLC PANEL (at DCS COS if in DCS MODE) |  |  |  |  |  |  | √ |  |  |  |
| - Start Purge Air heater/Fan (6 hours prior to start-up) |  |  |  |  |  | √ | √ |  |  |  |
| - Ensure no abnormal conditions observe at FAN/HEATERS |  |  |  |  |  |  | √ |  |  |  |

## START SEA WATER PUMP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| SEA WATER PUMP | P-1501A/ P-1501B/ P-1501C |  |  |  |  |  |  |  |  |  |
| - Ensure SWP soft starter and CB are in reset position ( CB ready to close) |  |  |  |  |  |  |  |  |  |  |
| - Check Sea Water inlet pool (fore bay) level (NL = 4m below GL) |  |  |  |  |  |  | √ |  |  |  |
| - Check SWP oil level |  |  |  |  |  |  |  |  |  |  |
| - Ensure Trash screen and installed and area is free from trash |  |  |  |  |  |  |  |  |  |  |
| - SWP discharge valves is crack OPEN (10%) | V-SW1002 V-SW1004 V-SW1006 |  |  |  |  |  | √ |  |  |  |
| - Open Vent valve from SWP (Debris filter area) | V-SW1601 |  |  |  |  |  | √ |  |  |  |
| - Close Drain valve from SWP (Debris filter area) | V-SW1504 |  |  |  |  |  |  |  |  |  |
| - Inlet valve to condenser OPEN (100%) | V-SW1007 V-SW1008 |  |  |  |  |  | √ |  |  |  |
| - Close Drain valve inlet to condenser | V-SW1505 V-SW1506 |  |  |  |  |  | √ |  |  |  |
| - Open Vent valve inlet to condenser | V-SW1602 V-SW1603 |  |  |  |  |  | √ |  |  |  |
| - Close Drain valve outlet from condenser | V-SW1507 V-SW1508 |  |  |  |  |  | √ |  |  |  |
| - Open Vent valve outlet from condenser | V-SW1604 V-SW1605 |  |  |  |  |  | √ |  |  |  |
| - Outlet from condenser OPEN (22%) | V-SW1009 V-SW1010 |  |  |  |  |  | √ |  |  |  |
| - Open vent valve from Priming air ejector | V-PA1046 V-PA1047 V-PA1113 V-PA1114 |  |  |  |  |  | √ |  |  |  |
| - Ensure SWP in remote position and all permissive are satisfied |  |  |  |  |  | √ |  |  |  |  |
| - Initiate selected 1st SWP START with coordination to AO | P-1501A/ P-1501B/ P-1501C |  |  |  |  | √ | √ |  |  |  |
| - Monitor SWP’s parameters |  |  |  |  |  | √ | √ |  |  |  |
| - Current Starting Current – 500A Normal Current – 205 – 215A | II P1501A |  |  |  |  | √ |  |  |  |  |
| - Temperature Bearing Temp = <100C Winding Temp = <155C | TI SW 1501A3/ TI SW1501A4 |  |  |  |  | √ |  |  |  |  |
| - Pressure Discharge Pressure = 2.2 ksc – 2.8 ksc | PG SW1501A/ PG SW1501B/ PG SW1501C |  |  |  |  | √ | √ |  |  |  |
| - Vibration Motor Vibration = <12 mm/s | VI SW1501 A1/ VI SW 1501A2 |  |  |  |  | √ |  |  |  |  |
| - Close vent valve when water comes out 1st debris filter | V-SW1601 V-PA1046 V-PA1047 V-PA1113 V-PA1114 |  |  |  |  |  | √ |  |  |  |
| - Adjust SWP discharge valve opening to attain 2.2 ksc – 2.4 ksc | V-SW1002/ V-SW1004/ V-SW 1006 |  |  |  |  | √ | √ |  |  |  |
| - START 2nd Selected SWP with coordination to AO | P-1501A/ P-1501B/ P-1501C |  |  |  |  | √ | √ |  |  |  |
| - Monitor SWP’s parameters |  |  |  |  |  | √ | √ |  |  |  |
| - Current Starting Current – 500A Normal Current – 205 – 215A | II P1501A |  |  |  |  | √ |  |  |  |  |
| - Temperature Bearing Temp = <100C Winding Temp = <155C | TI SW 1501A3/ TI SW1501A4 |  |  |  |  | √ |  |  |  |  |
| - Pressure Discharge Pressure = 2.2 ksc – 2.8 ksc | PG SW1501A/ PG SW1501B/ PG SW1501C |  |  |  |  |  | √ |  |  |  |
| - Current Starting Current – 500A Normal Current – 205 – 215A | VI SW1501 A1/ VI SW 1501A2 |  |  |  |  | √ |  |  |  |  |
| - Adjust SWP discharge valve opening to attain 2.2 – 2.4 ksc | V-SW1002/ V-SW1004/ V-SW 1006 |  |  |  |  | √ | √ |  |  |  |
| - Ensure the line is properly vented (Continuous flow of Seawater coming out of vent). Then CLOSE Air supply valve from PRIMING EJECTOR and Water box vent valves |  |  |  |  |  |  | √ |  |  |  |
| - Adjust condenser outlet valve to 40%. Check the pressure at Condenser INLET water box must be 1.0 to 1.1 Kg/cm². | V-SW 1007/ V-SW 1008 |  |  |  |  | √ | √ |  |  |  |
| - Ensure 0.4 Kg/cm² difference between inlet and outlet of condenser | PI SW 1110A1/ PI SW 1110A2 and PI SW1110B1/ PI SW1110B2 |  |  |  |  | √ | √ |  |  |  |
| - Set the standby SWP to AUTO |  |  |  |  |  | √ |  |  |  |  |
| - Set Standby SWP discharge valve to same as discharge valve of the running SWP | V-SW1002 V-SW1004 V-SW1006 |  |  |  |  |  |  |  |  |  |

## START HYPO CHLORINATED PUMP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| HYPO CHLORINATION DOSING PUMP Check procedure at WT | P-0761A/ P-0761B and P-0762A/ P-0762B |  |  |  |  | √ | √ | √ |  |  |
| - Ensure all pump permissive satisfied and Initiated START Hypo chlorination dosing pump | P-0761A/ P-0761B and P-0762A/ P-0762B |  |  |  |  | √ | √ | √ |  |  |
| - Ensure pump is running at local |  |  |  |  |  |  | √ | √ |  |  |
| - Check for pump discharge pressure | PG- check at local |  |  |  |  |  | √ | √ |  |  |

## START DEBRIS FILTER

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| DEBRIS FILTER | S- 1502 |  |  |  |  | √ | √ | √ |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  |  |  | √ | √ |  |  |
| - Ensure all permissive are satisfied and Set debris filter to auto start | Input cut in (DP conditions) |  |  |  |  | √ | √ |  |  |  |

## SEA WATER BOOSTER PUMP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| SEA WATER BOOSTER PUMP | P-1503A/ P-1503B/ P-1503C |  |  |  |  | √ | √ |  |  |  |
| - Ensure that the SWBP breaker is RACKED-IN and in CLOSE position in LV MCC |  |  |  |  |  |  |  |  |  |  |
| - Check that the SWBP suction pressure is within limit (1~1.1 ksc) |  |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position, line is fully prime prior to start up). - SWBP inlet valve 100% open - SWBP outlet valve 5% open to allow line venting (Auto-vent). | AO refer to valve PRE-Start Checklist |  |  |  |  |  | √ |  |  |  |
| - Ensure all SWBP’s permissive are satisfied |  |  |  |  |  | √ |  |  |  |  |
| - Initiate START to 1st selected Sea Water Booster Pump with proper coordination to AO | P-1503A/ P-1503B/ P-1503C |  |  |  |  | √ | √ |  |  |  |
| - Check pump running in local | P-1503A/ P-1503B/ P-1503C |  |  |  |  |  | √ |  |  |  |
| - Ensure SWBP Inlet Pressure is at 1.0 ksc |  |  |  |  |  | √ | √ |  |  |  |
| - Monitor SWBP’s parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current (Amps) |  | 90 | 120 | 126 |  |  |  |  |  |  |
| - Temperature(°C) |  |  |  |  |  |  |  |  |  |  |
| - Pressure (Kg/cm²) |  | 2.2-2.4 | <2.2 |  |  |  |  |  |  |  |
| - If pump is running in its operating speed - Slowly open the selected SWBP discharge valve (V-SW1016/V-SW1018/V-SW1020) until it reaches 2.3-2.4 Kg/cm² discharge pressure (PG SW1503A/ PG SW1503B/ PG SW1503C) | V-SW1016/V-SW1018/V-SW1020 PG SW1503A/ PG SW1503B/ PG SW1503C |  |  |  |  | √ | √ |  |  |  |
| - Initiate START to 2nd selected Sea Water Booster Pump with proper coordination to AO. - Note: Before starting the pump fill the line (Auto vent). | P-1503A/ P-1503B/ P-1503C |  |  |  |  | √ | √ |  |  |  |
| - Check pump running in local | P-1503A/ P-1503B/ P-1503C |  |  |  |  |  | √ |  |  |  |
| - If pump is running in its operating speed, Slowly open the selected SWBP discharge valve (V-SW1016/V-SW1018/V-SW1020) until it reaches 2.3-2.4 Kg/cm² discharge pressure (PG SW1503A/ PG SW1503B/ PG SW1503C) | V-SW1609 V-SW1016/V-SW1018/V-SW1020 PG SW1503A/ PG SW1503B/ PG SW1503C |  |  |  |  | √ | √ |  |  |  |
| - Set the standby SWBP to AUTO |  |  |  |  |  | √ |  |  |  |  |

## DEBRIS FILTER

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| DEBRIS FILTER | S-1504 |  |  |  |  | √ | √ |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position, line are fully prime prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  |  | √ | √ |  |  |  |
| - Ensure all permissive are satisfied and Set debris filter to auto start | Input cut in (DP conditions) | 20mBar | 80mBar |  |  | √ |  |  |  |  |

## MAKE UP WATER PUMP/ EXPANSION TANK FILLING

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| MAKE UP WATER PUMP | M-0709A/ M-0709B/ M-0709C |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  | √ | √ | √ |  |  |  |
| - Check if Demineralized Water Tank (T-0708A/B) at Normal Operating Level (>2 m) | T-0708A/ T-0708B |  |  |  |  | √ | √ |  |  |  |
| - Verify the ff: - Make-up Pump Suction Valve (V-MU0003/V-MU0004/V-MU0005) is OPEN - Discharge Valve (V-MU0007/V-MU0009/V-MU0011) is CLOSE - Make-up Pump Recirculation Valve (V-MU0013/V-MU0015/V-MU0017) is OPEN. | V-MU0003/V-MU0004/V-MU0005; V-MU0007/V-MU0009/V-MU0011; V-MU0013/V-MU0015/V-MU0017 |  |  |  |  |  | √ |  |  |  |
| - Ensure make-up pump in remote position and all permissive are satisfied. | M-0709A/ M-0709B/ M-0709C |  |  |  |  | √ |  |  |  |  |
| - Initiate START to selected MWP |  |  |  |  |  | √ |  |  |  |  |
| - Open gradually the MWP discharge valve until fully open |  |  |  |  |  | √ |  |  |  |  |
| - Monitor MWP’s parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current |  | 20 A | 61.1A |  |  | √ |  |  |  |  |
| - Temperature |  | - | - |  |  | √ |  |  |  |  |
| - Pressure |  | 10 ksc | 6.5 ksc |  |  | √ |  |  |  |  |
| - Vibration |  |  |  |  |  |  |  |  |  |  |
| - OPEN the discharge valve of one Standby Make-up Pump and Set the Pump to AUTO. | V-MU0007/V-MU0009/V-MU0011 |  |  |  |  | √ | √ |  |  |  |
| EXPANSION TANK FILLING | T-1109 |  |  |  |  |  |  |  |  |  |
| - Ensure Expansion tank inlet valve is open ( V-MU1031 and V-MU1032) | V-MU1031 and V-MU1032 |  |  |  |  |  | √ |  |  |  |
| - Open Expansion tank automatic inlet valve (XV – MU1109 if instrument air is available) or Bypass valve V-MU1033 to fill the tank at NL = 1.7m; Ensure HEADER PRESSURE of make-up line is > 6.0 Kg/cm², close the valve if the filling is OK | XV-MU1109; V-MU1033 |  |  |  |  | √ | √ |  |  |  |
| CLOSE COOLING LINE PRIMING |  |  |  |  |  |  |  |  |  |  |
| - Close all drains of the close cooling lines (refer to Valve checklist performed and accomplished by AO | Refer to AO Valve checklist |  |  |  |  |  | √ |  |  |  |
| - Ensure that valve line up is done. | Refer to AO Valve checklist |  |  |  |  |  |  |  |  |  |
| - Open Expansion tank outlet valve to prime the close cooling line (V-CW1001) | V-CW1001 |  |  |  |  |  | √ |  |  |  |
| - Open cooling line vents (V-AV1001, V-AV1002, V-AV1003, V-AV1004 and Air pre heater vents) Note: see checklist for reference | V-AV1001, V-AV1002, V-AV1003, V-AV1004 |  |  |  |  |  | √ |  |  |  |
| - Close all vents if close cooling line is fully primed, Ensure Expansion tank is at NL = 1.7m and make up if necessary | V-AV1001, V-AV1002, V-AV1003, V-AV1004 |  |  |  |  | √ | √ |  |  |  |
| - Set Expansion tank inlet valve (XV-MU1109) to AUTO if instrument air is available. | XV-MU1109 |  |  |  |  | √ |  |  |  |  |

## AUXILLIARY COOLING WATER PUMP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| AUXILLIARY COOLING WATER PUMP | P-1108A/ P-1108B |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  |  | √ | √ |  |  |  |
| - Ensure that all permissive are satisfied. | P-1108A/ P-1108B |  |  |  |  | √ |  |  |  |  |
| - Set the LCP (Local Control Panel) of both selected and standby ACWP to remote position | P-1108A/ P-1108B |  |  |  |  | √ | √ |  |  |  |
| - Open the selected ACWP discharge valve to 5% | V-CW1007/ V-CW1009 |  |  |  |  |  | √ |  |  |  |
| - Initiate START of the selected AWCP with proper coordination to AO |  |  |  |  |  | √ |  |  |  |  |
| - Monitor ACWP parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current |  | 30A | 33.7 |  |  |  |  |  |  |  |
| - Strainer Differential pressure | DPI-CW1108A/ DPI-CW1108B | 0.4~0.5 ksc | 0.55 ksc | 0.8 ksc |  |  |  |  |  |  |
| - If pump running at full speed, gradually open the discharge valve until it reaches 7 Kg/cm² | PG-CW1108A/ PG-CW1108B |  |  |  |  |  | √ |  |  |  |
| - Set the discharge valve of the standby ACWP same as the % opening of the running ACWP. | V-CW1007/ V-CW1009 |  |  |  |  | √ | √ |  |  |  |
| - Ensure that cooling water was establishing to |  |  |  |  |  |  | √ |  |  |  |
| - Turbine cooler |  |  |  |  |  |  |  |  |  |  |
| - Generator air cooler |  |  |  |  |  |  |  |  |  |  |
| - BFP cooling system |  |  |  |  |  |  |  |  |  |  |
| - Bottom ash screw cooler |  |  |  |  |  |  |  |  |  |  |
| - PAF oil cooler |  |  |  |  |  |  |  |  |  |  |
| - SAF bearing cooling |  |  |  |  |  |  |  |  |  |  |
| - GAH |  |  |  |  |  |  |  |  |  |  |
| - IDF cooling system |  |  |  |  |  |  |  |  |  |  |
| - PA Compressor/Dryer cooling system |  |  |  |  |  |  |  |  |  |  |
| - Oil Coolers |  |  |  |  |  |  |  |  |  |  |
| - After cooler |  |  |  |  |  |  |  |  |  |  |
| - IA Compressor/Dryer cooling system |  |  |  |  |  |  |  |  |  |  |
| - Oil Coolers |  |  |  |  |  |  |  |  |  |  |
| - After cooler |  |  |  |  |  |  |  |  |  |  |
| - Sampling rack |  |  |  |  |  |  |  |  |  |  |
| - Set selected standby ACWP in AUTO |  |  |  |  |  | √ |  |  |  |  |

## INSTRUMENT AIR DRYER

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| INSTRUMENT AIR DRYER | D-0704A/ D-0704B/ D-0704C |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  |  | √ | √ |  |  |  |
| - Ensure that all permissive are satisfied. | D-0704A/ D-0704B/ D-0704C |  |  |  |  | √ | √ |  |  |  |
| - Ensure expansion tank is at NL 1.7m | T-1109 |  |  |  |  |  | √ |  |  |  |
| - At LCP panel Initiate ON to selected dryer with proper coordination to CRO | D-0704A/ D-0704B/ D-0704C |  |  |  |  |  |  |  |  |  |
| - Monitor Dryer parameters |  |  |  |  |  |  | √ |  |  |  |
| - Air Inlet Temperature (5°C ~ 50°C) | T1 |  |  |  |  |  |  |  |  |  |
| - Expansion Valve Outlet Temperature (5°C ~ 15°C) | T2 |  |  |  |  |  |  |  |  |  |
| - Condensing Temperature (15°C ~ 52°C) | T3 |  |  |  |  |  |  |  |  |  |
| - Discharge Temperature (40°C ~ 115°C) | T4 |  |  |  |  |  |  |  |  |  |
| - Suction Temperature (-5°C ~ 30°C) | T5 |  |  |  |  |  |  |  |  |  |
| - Evaporator Air Outlet Temperature (0°C ~ 45°C) | T6 |  |  |  |  |  |  |  |  |  |
| - Ambient/Water inlet Temperature(press T3 twice) (5°C ~ 40°C)/ (10°C ~ 38°C) | T7 |  |  |  |  |  |  |  |  |  |
| - Observe for at least 5mins for any abnormality and coordinate to CRO about the status of the dryer. |  |  |  |  |  |  |  |  |  |  |

## INSTRUMENT AIR COMPRESSOR/MOTOR

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| INSTRUMENT AIR COMPRESSOR/MOTOR Note: AT initial start-up, close the tank discharge valve at first and gradually open when the AC is running(fill air line gradually so that AC will not overload) | C-0704A/ C-0704B/ C-0704C M-0704A/ M-0704B/ M-0704C |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  | √ | √ | √ |  |  |  |
| - Ensure that all permissive are satisfied. |  |  |  |  |  | √ |  |  |  |  |
| - Ensure Lube oil tank level at NL = 300 L |  |  |  |  |  |  | √ |  |  |  |
| - OPEN the instrument air valve to supply instrument air in Blow-Off Valve Solenoid Valve and Oil Tank ejector, adjust filter pressure regulator to 0.5 MPa. (At Ambient Start-Up, Portable Compressor is used to supply instrument air) |  |  |  |  |  |  | √ |  |  |  |
| - Adjust the negative pressure in the Oil tank to 1.0-2.0 KPa A. |  |  |  |  |  |  | √ |  |  |  |
| - Turn on the Main Power of the starter, turn ON the circuit breaker and circuit protector in order of MCCB/ELCB-1 to MCCCB2 to MCCB3 to CP-4 and to CP-5 inside the compressor panel. |  |  |  |  |  |  |  |  |  |  |
| - Ensure the compressor is in Local Position. |  |  |  |  |  |  |  |  |  |  |
| - At LCP, START Auxiliary Oil Pump by pressing “ON” on Start preparation switch and set the load control to FORCE UNLOAD. Check the negative pressure in the oil tank. Make sure that there is no leakage at lubricating pipe joints and pump and valve. (AOP will permit to Start the Compressor after 20s) |  |  |  |  |  | √ |  |  |  |  |
| - Observe for at least 5mins for any abnormality and coordinate to CRO about the status of the compressor/motor. | C-0704A/ C-0704B/ C-0704C M-0704A/ M-0704B/ M-0704C |  |  |  |  | √ | √ |  |  |  |
| - Initiate RUN with proper coordination to CRO |  |  |  |  |  | √ | √ |  |  |  |
| - Ensure Auxiliary oil pump will stop after 40 secs |  |  |  |  |  | √ | √ |  |  |  |
| - Check for compressor/motor parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current |  |  |  |  |  |  |  |  |  |  |
| - Temperature |  |  |  |  |  |  |  |  |  |  |
| - Vibration |  |  |  |  |  |  |  |  |  |  |
| - Set the load control to AUTO |  |  |  |  |  | √ |  |  |  |  |

## PLANT AIR DRYER

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| INSTRUMENT AIR DRYER Note: AT initial start-up, close the tank discharge valve at first and gradually open when the AC is running(fill air line gradually so that AC will not overload) | D-0704A/ D-0704B/ D-0704C |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  | √ | √ | √ |  |  |  |
| - Ensure that all permissive are satisfied. | D-0704A/ D-0704B/ D-0704C |  |  |  |  | √ | √ |  |  |  |
| - Ensure expansion tank is at NL 1.7m | T-1109 |  |  |  |  |  | √ |  |  |  |
| - At LCP panel Initiate ON to selected dryer with proper coordination to CRO | D-0704A/ D-0704B/ D-0704C |  |  |  |  |  |  |  |  |  |
| - Monitor Dryer parameters |  |  |  |  |  |  | √ |  |  |  |
| - Air Inlet Temperature (5°C ~ 50°C) | T1 |  |  |  |  |  |  |  |  |  |
| - Expansion Valve Outlet Temperature (5°C ~ 15°C) | T2 |  |  |  |  |  |  |  |  |  |
| - Condensing Temperature (15°C ~ 52°C) | T3 |  |  |  |  |  |  |  |  |  |
| - Discharge Temperature (40°C ~ 115°C) | T4 |  |  |  |  |  |  |  |  |  |
| - Suction Temperature (-5°C ~ 30°C) | T5 |  |  |  |  |  |  |  |  |  |
| - Evaporator Air Outlet Temperature (0°C ~ 45°C) | T6 |  |  |  |  |  |  |  |  |  |
| - Ambient/Water inlet Temperature(press T3 twice) (5°C ~ 40°C)/ (10°C ~ 38°C) | T7 |  |  |  |  |  |  |  |  |  |
| - Observe for at least 5mins for any abnormality and coordinate to CRO about the status of the dryer. |  |  |  |  |  |  |  |  |  |  |

## PLANT AIR COMPRESSOR/MOTOR

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| INSTRUMENT AIR COMPRESSOR/MOTOR | C-0704A/ C-0704B/ C-0704C M-0704A/ M-0704B/ M-0704C |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to start up) | AO refer to valve PRE-Start Checklist |  |  |  | √ | √ | √ |  |  |  |
| - Ensure that all permissive are satisfied. |  |  |  |  |  | √ |  |  |  |  |
| - Ensure Lube oil tank level at NL = 300 L |  |  |  |  |  |  | √ |  |  |  |
| - OPEN the instrument air valve to supply instrument air in Blow-Off Valve Solenoid Valve and Oil Tank ejector, adjust filter pressure regulator to 0.5 MPa. (At Ambient Start-Up, Portable Compressor is used to supply instrument air) |  |  |  |  |  |  | √ |  |  |  |
| - Adjust the negative pressure in the Oil tank to 1.0-2.0 KPa A. |  |  |  |  |  |  | √ |  |  |  |
| - Turn on the Main Power of the starter, turn ON the circuit breaker and circuit protector in order of MCCB/ELCB-1 to MCCCB2 to MCCB3 to CP-4 and to CP-5 inside the compressor panel. |  |  |  |  |  |  |  |  |  |  |
| - Ensure the compressor is in Local Position. |  |  |  |  |  |  |  |  |  |  |
| - At LCP, START Auxiliary Oil Pump by pressing “ON” on Start preparation switch and set the load control to FORCE UNLOAD. Check the negative pressure in the oil tank. Make sure that there is no leakage at lubricating pipe joints and pump and valve. (AOP will permit to Start the Compressor after 20s) |  |  |  |  |  | √ |  |  |  |  |
| - Observe for at least 5mins for any abnormality and coordinate to CRO about the status of the compressor/motor. | C-0704A/ C-0704B/ C-0704C M-0704A/ M-0704B/ M-0704C |  |  |  |  | √ | √ |  |  |  |
| - Initiate RUN with proper coordination to CRO |  |  |  |  |  | √ | √ |  |  |  |
| - Ensure Auxiliary oil pump will stop after 40 secs |  |  |  |  |  | √ | √ |  |  |  |
| - Check for compressor/motor parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current |  |  |  |  |  |  |  |  |  |  |
| - Temperature |  |  |  |  |  |  |  |  |  |  |
| - Vibration |  |  |  |  |  |  |  |  |  |  |
| - Set the load control to AUTO |  |  |  |  |  | √ | √ |  |  |  |

## TURBINE CONTROL OIL

## PRE-START CHECK

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Ensure that all Start-up Checks of the Turbine Lube and Control Oil System are finished |  |  |  |  | √ | √ | √ |  |  |  |
| - Closed Cooling System Completed and properly vented |  |  |  |  | √ | √ | √ |  |  |  |
| - Lube Oil Temp Control Valve change mode to Remote | ICVCW1201 |  |  |  |  | √ |  |  |  |  |
| - Verify temperature of Oil Outlet and Water Inlet of Lube Oil Cooler. NOTE: 37°C for the maximum temperature of Cooling Water at inlet. 46°C average temperature of Oil at outlet. | H-n921A/B |  |  |  |  |  | √ |  |  |  |
| - Check the tank Oil Level in the Main Oil Tank. | T-n920 | > 0 mm |  |  |  |  | √ |  |  |  |
| - Verify all drained valves going to the main oil tank are already closed. | V-LOn021 (NC) V-LOn032 (NC) |  |  |  |  |  | √ |  |  |  |
| - Verify all alarms at TCS are cleared |  |  |  |  |  | √ |  |  |  |  |

## MAIN OIL PUMP & VAPOR EXTRACTOR START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV |  | CRO | AO | WTP | MH |  |
| - Verify that Lube Oil Pressure Control Valve Sensing Line Adjusting Valve is open. | V-LOn031 |  |  |  |  |  |  | √ |  |  |  |
| - Verify that the U-seal of vapour extractor has been established |  |  |  |  |  |  |  | √ |  |  |  |
| - Crack Open the suction valve of vapour extractor | V-LOn041 | around 10° |  |  |  |  |  | √ |  |  |  |
| - Start the Vapour Extractor |  |  |  |  |  |  |  | √ |  |  |  |
| - Check the vacuum gauge on the main oil tank | PGLO1920 | -20 to -50mmH2O |  |  |  |  |  | √ |  |  |  |
| - Adjust the opening of suction valve of vapour extractor if necessary | V-LOn041 |  |  |  |  |  |  | √ |  |  |  |
| - Start one of the Main Oil Pump. | P-n922A or B |  |  |  |  |  | √ |  |  |  |  |
| - Check and observe the temperature of the Main Oil Tank. | T-n920 |  |  |  |  |  |  | √ |  |  |  |
| - Check that the Lube Oil Pressure is satisfactory. Check that all the Pressure Instruments show the normal value at Main Oil Pump outlet. | P-n922A/B | ~5.6 kg/cm2g -6.6 kg/cm2g |  |  |  |  |  | √ |  |  |  |
| - Check that no oil leakage of the lubricating oil system is observed |  |  |  |  |  |  |  | √ |  |  |  |
| - Check that the vibration, noise, starting and loading currents are satisfactory. |  |  |  |  |  |  | √ | √ |  |  |  |
| - Set Lube Oil Pressure by adjusting Lube Oil Pressure Control Valve if necessary | V-LOn004 |  |  |  |  |  |  | √ |  |  | With instrument tech |
| - Check that the flow sight shows normal oil flow from the oil side of the cooler |  |  |  |  |  |  |  | √ |  |  |  |
| - Check for the bearing Oil Pressure (3rd FL) | PGLO1008 | >1.05 ksc |  |  |  |  | √ | √ |  |  |  |
| - Check that the Bearing Drain Oil (3rd fl) on each flow sight is satisfactory. |  |  |  |  |  |  |  | √ |  |  |  |
| - Check that the condition of the Lubrication Oil supplied to bearing is available for the unit operation. |  |  |  |  |  |  |  | √ |  |  |  |
| Note: Bearing Oil Temperature is: - Between 27 to 40°C during Turning Operation (0 to 4 RPM). - Between 27 to 50°C when Rotor Speed is within Turning Speed and Rated Speed (4 to 3600 RPM). - Between 40 to 50°C during Rated Rotor Speed (3600 RPM). |  |  |  |  |  |  |  |  |  |  |  |

## OIL PURIFIER START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Drained any accumulated water | V-LO1223 (NC) |  |  |  |  |  | √ |  |  |  |
| - Verify that the Oil Purifier Inlet Oil Supply Connection Valve is open. | V-LOn201 (NO) |  |  |  |  |  | √ |  |  |  |
| - Verify that the Coalescer Filter Inlet Valve is open. | V-LOn205 (NO) |  |  |  |  |  | √ |  |  |  |
| - Start the Oil Purifier Pump | P-n941 |  |  |  |  | √ |  |  |  |  |
| - Check that the vibration, noise, starting and loading currents, and discharge pressure are satisfactory. |  | P ~ 2.96ksc |  |  |  | √ | √ |  |  |  |
| - Check for presence of leaks. |  |  |  |  |  |  | √ |  |  |  |
| NOTE: The Oil Purifier Unit can operate either intermittently or continuously as required. Sampling of Lube and Control Oil shall be acquired and analyzed on a regular basis. |  |  |  |  |  |  |  |  |  |  |

## CONTROL OIL PUMP START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Verify that Main Oil Pump is running within normal pressure. | P-n922A/B | ≤ 5.6 kg/cm2g |  |  |  | √ | √ |  |  |  |
| - Start one of the Control Oil Pump. | P-n931A/B |  |  |  |  | √ |  |  |  |  |
| - Check that all the pressure instruments show the normal value approximately at Control Oil Pump outlet. | P-n931A/B | 163.2 ksc |  |  |  |  | √ |  |  |  |
| - Check that the vibration, noise, starting and loading currents are satisfactory. |  |  |  |  |  | √ | √ |  |  |  |
| - Check that the Control Oil Pressure is satisfactory. NOTE: When operating switches of the following pumps are set to “Auto” position, these pumps start automatically on the conditions below: - Main Oil Pump (MOP) (P-n922A/B) Main oil pump (running) discharge pressure ≤ 5.6 kg/cm2g - Control Oil Pump (COP) (P-n931A/B) Control oil pump (running) discharge pressure ≤ 133 kg/cm2g - Emergency Oil Pump (EOP) - Bearing oil pressure ≤ 1.05 kg/cm2g Stop function is carried out by manual operation. |  | ~133 ksc -163 ksc |  |  |  | √ | √ |  |  |  |

## ROTARY AIR PRE-HEATER

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| ROTARY AIR PRE-HEATER | H-1052 |  |  |  |  |  |  |  |  |  |
| - Ensure biasing dampers are closed |  |  |  |  |  | √ | √ |  |  |  |
| - Ensure soot blower lance is in retract position |  |  |  |  |  |  | √ |  |  |  |
| - Ensure that air pre heater inverter drive in REMOTE mode |  |  |  |  |  | √ | √ |  |  |  |
| - Ensure Firefighting system is available |  |  |  |  |  |  | √ |  |  |  |
| - Ensure Plant air is available |  |  |  |  |  |  | √ |  |  |  |
| - Ensure cooling system is available |  |  |  |  |  |  | √ |  |  |  |
| - Ensure that all permissive are satisfied. |  |  |  |  |  | √ |  |  |  |  |
| - Initiate START air pre-heater drive motor |  |  |  |  |  | √ |  |  |  |  |
| - Check Air Pre-Heater parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current | IIFA 1052M1 | 4.3 A | 12A |  |  | √ |  |  |  |  |
| - Set the Air Drive to AUTO |  |  |  |  |  | √ | √ |  |  |  |
| - Open Biasing damper to 100% at Reheater and Superheater side |  |  |  |  |  |  | √ |  |  |  |

## CONDENSER HOT WELL FILLING/PRIMING/RECIRCULATION

NOTE: CHEMICAL DOSING AND SAMPLING RACK UP START UP c/o WATER TREATMENT conducted prior to condenser hot well filling/recirculation/priming

Refer to: XIII- Guidelines on water steam systems

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| CONDENSER HOTWELL | H-1110 |  |  |  |  |  |  |  |  |  |
| - Ensure make up pump is running | P-0709A/ P-0709B/ P-0709C |  |  |  |  |  |  |  |  |  |
| - Ensure valve line up (please see condenser hotwell filling pre-start checklist) is properly executed and with close coordination to Auxiliary operator. | V-MU0007/V-MU0009/V-MU0011 |  |  |  |  |  |  |  |  |  |
| - Fill condenser hotwell up to (NL= 0mm), use hotwell level control valve LCV-MU1110 and hotwell filling motorized valve MV-MU1001 then fully drain using condenser hotwell manual drain valve V-CD1083 TWICE to flush out remaining foreign material. Ensure MWP discharge header pressure at DCS (>6.5Kg/cm2) | V-MU1023 |  |  |  |  |  | √ |  |  |  |
| - Monitor parameters |  |  |  |  |  |  |  |  |  |  |
| - Current of MWP |  |  |  |  |  |  |  |  |  |  |
| - Discharge pressure of MWP |  |  |  |  |  |  |  |  |  |  |
| - Hotwell Level |  |  |  |  |  |  |  |  |  |  |
| - Close hotwell level control valve and hotwell filling motorized valve once level is reached at (NL=+150mm) and set LCV-MU1110 to AUTO with SV of at least (+100mm) in preparation for hotwell to hotwell water conditioning |  |  |  |  |  |  | √ |  |  |  |
| CONDENSATE LINE PRIMING |  |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to PRIMING) | Refer to AO valve checklist |  |  |  |  |  | √ |  |  |  |
| - After priming the Condensate pump discharge line, CLOSE Steam Jet Air Ejector Condenser Vent Valves (V-CD1359/V-CD1360) and Gland Steam Condenser Discharge Line Vent Valves (V-CD1641/V-CD1642) then shut-off Deaerator Initial Filling Valve (V-MU1027) and CLOSE Condensate Pump Drain Valve (V-CD1516/V-CD1517) | V-CD1359/V-CD1360; V-CD1641/V-CD1642; V-MU1027; V-CD1516/V-CD1517 |  |  |  |  |  | √ |  |  |  |
| CONDENSATE RECIRCULATION/WATER CONDITIONING |  |  |  |  |  |  |  |  |  |  |
| - Ensure all valve line ups are accomplished. (valve position prior to CEP start up) | Refer to AO valve checklist |  |  |  |  |  | √ |  |  |  |
| - Ensure all start up permissive are satisfied (strainer ΔP = < 0.8ksc) |  |  |  |  |  | √ |  |  |  |  |
| - SET Condenser Recirculation Valve FCV-CD1120 to MANUAL and ADJUST to 60% Opening. | FCV-CD1120 |  |  |  |  | √ | √ |  |  |  |
| - Initiate START to selected CEP with proper coordination to AO | P-1116A/P-1116B |  |  |  |  | √ |  |  |  |  |
| - Monitor parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current of CEP |  | 25A | 37A |  |  |  |  |  |  |  |
| - At full speed , fully open discharge valve of selected CEP and set the standby CEP to REMOTE/AUTO |  |  |  |  |  | √ |  |  |  |  |
| - Open Condenser Recirculation Valve FCV-CD1120 to increase condensate flow to 150 T/H. Set SV to 150 T/H and Set to AUTO. |  |  |  |  |  |  |  |  |  |  |
| - Open V-CD1047 Inlet valve (from CHEMICALS (NEUTRAL AMINE, CARBO HYDRAZIDE AND PHOSPATE) | V-CD1047 |  |  |  |  |  | √ |  |  |  |
| - OPEN V-CH1001 and V-CH1003 Inlet valve (from NEUTRAL AMINE) | V-CH1001 and V-CH1003 |  |  |  |  |  | √ |  |  |  |
| - START Injection of NEUTRALIZING AMINE and Recirculate from Hotwell to Hotwell through Condenser Recirculation Valve (FCV-CD1120). NOTE: Coordinate Nuetral Amine Injection with Water Treatment. |  |  |  |  |  | √ | √ |  |  |  |
| - Initiate START of dosing pump of CHEMICAL (NEUTRAL AMINE) at chemical dosing system. |  |  |  |  |  | √ |  |  |  |  |
| - Monitor parameters |  |  |  |  |  | √ |  |  |  |  |
| - Condensate conductivity |  |  |  |  |  |  |  |  |  |  |
| - PH |  |  |  |  |  |  |  |  |  |  |
| - Iron Content |  |  |  |  |  |  |  |  |  |  |
| Note: Once the water conditioning is already done- prepare for deaerator filling |  |  |  |  |  |  |  |  |  |  |

## DEAERATOR FILLING AND CHEMICAL RECIRCULATION

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| DEAERATOR FILLING |  |  |  |  |  |  |  |  |  |  |
| - Ensure all valves line up are accomplished by AO prior to Deaerator filling. | Refer to AO valve checklist |  |  |  |  | √ | √ |  |  |  |
| - Ensure Hot well water level is at NL = 0mm and PH level = 8.6 – 9.2 | LI-CD11041/LI-CD11042/LI-CD11043 |  |  |  |  | √ |  |  |  |  |
| - Initiate Deaerator filling, slowly open Deaerator Level Control Valve (LCV – CD1104). NOTE: - During Water Conditioning, drain water from deaerator through BFP A/B Pump Casing. - Pipe Hammering may be noticed when LCV opening decreases to 2- 3%. | LCV-CD1104; FCV-CD1120 |  |  |  |  | √ | √ |  |  |  |
| - Fill up Deaerator until level increased to NL = +-100 mm. Initiate flushing using BFWP A and B Pump casing drain while maintaining Deaerator level. |  |  |  |  |  |  |  |  |  |  |
| - Gather water sample at Deaerator local level gauge drain and BFWP Pump casing drain line. Monitor parameters with coordination to Water Treatment: |  |  |  |  |  |  |  |  |  |  |
| - pH | V-CH1005 |  |  |  |  |  |  |  |  |  |
| - Fe content |  |  |  |  |  |  | √ |  |  |  |
| - Hotwell Level | XV-CD1104-2 |  |  |  |  |  | √ |  |  |  |
| - Deaerator Level |  |  |  |  |  |  |  |  |  |  |
| - Once water quality is within the specified parameters, OPEN Carbohydrazide chemical injection isolation valve. | V-CH1005 |  |  |  |  |  | √ |  |  |  |
| - Start Chemical Injection Pump for Carbohydrazide with coordination to water treatment. |  |  |  |  |  |  | √ |  |  |  |
| - Open Emergency Drain to Condenser Valve (XV-CD1104-2) for recirculation of feed water from Deaerator back to Condenser for thorough mixing of chemicals. NOTE: Do not open emergency drain to Hotwell if water conditioning is not yet finished | XV-CD1104-2 |  |  |  |  |  | √ |  |  |  |
| - CLOSE Emergency Drain to Condenser Valve (XV-CD1104-2) when Level of Deaerator is at (NWL= 0mm) in preparation for steam drum filling. | XV-CD1104-2 |  |  |  |  |  | √ |  |  |  |
| - pH |  | 8.6~9.2 |  |  |  |  |  | √ |  |  |
| - Fe content |  | <250 ppb | 250 ppb |  |  |  |  | √ |  |  |
| - Hotwell Level |  | 0~100mm | -150 mm | -300 mm |  | √ |  |  |  |  |
| - Deaerator level |  | 0~100 mm |  |  |  | √ |  |  |  |  |
| - Set Deaerator Level control valve (LCV-CD1104) to AUTO with SV of 0mm. | LCV-CD1104 |  |  |  |  | √ |  |  |  |  |

## STEAM DRUM FILLING

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| STEAM DRUM FILLING | T-1001 |  |  |  |  |  |  |  |  |  |
| - Ensure all valves line up are accomplished by AO prior to Steam Drum filling. Note: Ensure MS BLOW OFF VALVE (BOV)= >10% OPEN | Refer to AO valve checklist |  |  |  | √ |  | √ |  |  |  |
| - Ensure Deaerator is at NWL | LI-CD11041/LI-CD11042/LI-CD11043 |  |  |  |  | √ |  |  |  |  |
| - Ensure Hotwell water level is at NL = 0mm and PH level = 9.0 |  |  |  |  |  | √ |  |  |  |  |
| - Ensure Pre-start check conducted and accomplished by AO prior start of BFP | Refer to AO valve checklist |  |  |  |  |  | √ |  |  |  |
| - Ensure all permissive are satisfied prior start of BFP |  |  |  |  |  |  |  |  |  |  |
| - Initiate START of LOP of BFP A/B | LOP A/LOP B |  |  |  |  | √ |  |  |  |  |
| - Monitor parameters |  |  |  |  |  | √ | √ |  |  |  |
| - Oil Temperature |  |  |  |  |  |  | √ |  |  |  |
| - Oil Pressure |  |  |  |  |  |  | √ |  |  |  |
| - Differential Oil Pressure |  |  |  |  |  |  | √ |  |  |  |
| - Set the selected standby BFP LOP to AUTO | LOP A/LOP B |  |  |  |  | √ |  |  |  |  |
| - Verify the following: - HPH1 and HPH2 Heater inlet (V-FW1009/V-FW1010) are OPEN - Outlet valve (V-FW1012/V-FW1013) are OPEN - Bypasses (V-FW1011/V-FW1014) are CLOSED | V-FW1009/V-FW1010 ; V- FW1012/V-FW1013 V-FW1011/V-FW1014 |  |  |  |  |  | √ |  |  |  |
| - Verify Feed Water Regulator Bypass valve is CLOSED (V-FW1017). | V-FW1017 |  |  |  |  | √ | √ |  |  |  |
| - Fully OPEN BFPs suction (V-FW1002/V-FW1001) to fill up pump suction lines. Check if the limit switch is touched. | V-FW1001/V-FW1002 (FW1031/FW1032) |  |  |  |  | √ | √ |  |  |  |
| - Verify the following: - Main Discharge Valve is closed - Discharge Valve Equalizing Valve is closed | MV-F1001 / MV-FW1002 MV-FW1391 / MV-FW1392 |  |  |  |  |  | √ |  |  |  |
| - Verify minimum flow valve (V-FW1007/FW1008) and balance valve (V-FW1044/V-FW1046) are open. | V-FW1007/FW1008 / V-FW1044/V-FW1046 |  |  |  |  |  | √ |  |  |  |
| - Verify that the startup permissive for Boiler Feed Pump is satisfied |  |  |  |  |  |  |  |  |  |  |
| - Initiate START to selected BFP with proper coordination with the AO | P-1115A/ P-1115B |  |  |  |  | √ |  |  |  |  |
| - Monitor parameters and ensure parameters are stable |  |  |  |  |  | √ |  |  |  |  |
| - Current |  |  |  |  |  |  |  |  |  |  |
| - Vibration |  |  |  |  |  |  |  |  |  |  |
| - Differential Pressure | DPI FW1115A/ DPI FW1115B |  |  |  |  |  |  |  |  |  |
| - Gradually OPEN the Equalizing Discharge Motorized Valve (MV-FW1391/MV-FW1392) of Selected BFP (thru inching when outlet pipe has not yet prime to equalize the pressure of inlet and outlet and to avoid hammering). | MV-FW1391/MV-FW1392 |  |  |  |  | √ |  |  |  |  |
| - When Discharge Pressure (PI-FW1011) reached >200 Kg/cm2, OPEN the Main Discharge Motorized Valve (MV-FW1001/MV-FW1002) up to 100% OPENING. Close the Equalizing Valve if the main discharge valve is fully OPEN. | PI-FW1011; MV-FW1001/MV-FW1002 |  |  |  |  | √ |  |  |  |  |
| - SET FCV-FW1130-2 to MANUAL and Gradually OPEN. NOTE: Max Differential Temperature between economizer water outlet and Drum Metal Temperature = 110℃ | FCV-FW1130-2 |  |  |  |  | √ |  |  |  |  |
| - OPEN V-CH1007 and Start Phosphate Dosing pump to inject phosphate to feed water with coordination with Water Treatment. NOTE: Do not start Phosphate Injection if Water Conditioning is not yet finished. |  |  |  |  |  |  |  |  |  |  |
| - Monitor parameters |  |  |  |  |  |  |  |  |  |  |
| - Water quality |  |  |  |  |  |  |  |  |  |  |
| - Drum level (-150mm) |  |  |  |  |  |  |  |  |  |  |

## OIL SYSTEM CIRCULATION

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| OIL SYSTEM CIRCULATION | T-0701 |  |  |  |  |  |  |  |  |  |
| - Check Diesel Tank Level. Ensure level is >0.2m. |  |  |  |  | √ |  | √ |  |  |  |
| - Ensure all valves line up are accomplished by AO prior oil circulation. | Refer to AO Checklist |  |  |  |  | √ |  |  |  |  |
| - Ensure Tank Outlet isolation valve (V-DO0003) is OPEN. | V-DO0003 |  |  |  |  | √ |  |  |  |  |
| - Ensure Strainer Inlet Isolation valve (V-DO0004) is OPEN | V-DO0004 |  |  |  |  |  |  |  |  |  |
| - OPEN the Suction (V-DO0015) and Discharge (V-DO0017) valve of Selected and Standby Diesel Oil Pump. | V-DO0015; V-DO0017 |  |  |  |  |  |  |  |  |  |
| - Fully OPEN Diesel Oil Tank Recirculation Valve (PCV-DO0002). | PCV-DO0002 |  |  |  |  |  |  |  |  |  |
| - Fully OPEN Diesel Oil Tank Return Valve (PCV-DO100). |  |  |  |  |  |  |  |  |  |  |
| - Fully OPEN FCV-DO1012 and Set to manual. Make sure bypass line is CLOSE. |  |  |  |  |  | √ |  |  |  |  |
| - Ensure all Start permissive of Selected Diesel Oil Pump are satisfied in DCS. |  |  |  |  |  | √ |  |  |  |  |
| - Initiate START on selected Diesel oil pump. (M-0702A/M-0702B) with proper coordination to AO. | M-0702A/M-0702B |  |  |  |  | √ | √ |  |  |  |
| - Monitor Motor parameters |  |  |  |  |  | √ |  |  |  |  |
| - Current (II-P0702A/II-PO0702B) | II-P0702A/II-PO0702B |  |  |  |  |  |  |  |  |  |
| - Strainer DP (DPI-D00001) | DPI-D00001 |  |  |  |  |  |  |  |  |  |
| - Set standby diesel oil pump to AUTO |  |  |  |  |  | √ |  |  |  |  |
| - Decrease opening of PCV-DO0002 to increase Diesel Oil Pressure. |  |  |  |  |  | √ |  |  |  |  |
| - Throttle Diesel Oil Recirculation Pressure Control Valve (PCV-DO0002) in Manual Control depending on desired pressure. | PCV-DO0002 |  |  |  |  | √ |  |  |  |  |
| - Pressure (PI-D00005= 12.5Kg/cm²) |  |  |  |  |  |  |  |  |  |  |
| - Throttle Diesel Oil Recirculation Pressure Control Valve (PCV-D01009) in Manual Control depending on desired pressure. | PCV-D01009 |  |  |  |  | √ |  |  |  |  |
| - Pressure (PI-D01008 = 10.4Kg/cm²). |  |  |  |  |  |  |  |  |  |  |
| - Set PCV-DO0002 and PCV-DO1009 to AUTO when current values of PI-DO0005 and PI-DO1008 are near the set value of the PCVs. |  |  |  |  |  | √ |  |  |  |  |
| Note: Do not put PCV’s (PCV-DO0002 and PCV-DO1009) to auto during initial opening to avoid VALVE HUNTING. |  |  |  |  |  | √ | √ |  |  |  |
| - Check for any abnormalities and leaks |  |  |  |  |  | √ | √ |  |  |  |
| Diesel oil circulation is done – prepare for Draft system start up Note: PCVDO0002-55.4% OPEN, PCVDO1012 – 103% OPEN (for Ref.) |  |  |  |  |  |  |  |  |  |  |

## DRAFT SYSTEM PREPARATION AND START UP

## IDF START UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| IDF START UP | F1056 |  |  |  |  |  |  |  |  |  |
| - Ensure all valves line up are accomplished by AO prior to IDF start |  |  |  |  |  |  | √ |  |  |  |
| - Verify Cooling Water Pressure for bearing should be 0.5 to 2 kg/cm2. |  |  |  |  |  | √ | √ |  |  |  |
| - Check oil levels |  |  |  |  |  |  | √ |  |  |  |
| - Verify all gas side manholes/access are CLOSE. |  |  |  |  | √ |  | √ |  |  |  |
| - Ensure Secondary and Primary Air Damper are 100% OPEN. | FICFA1081/ FICFA1071 |  |  |  |  | √ | √ |  |  |  |
| - Ensure Biasing Damper of Superheater and Reheater Side are 100% OPEN. | HICHR1002A/ HICHR1002B |  |  |  |  | √ | √ |  |  |  |
| - Ensure IDF Damper is fully closed and hydraulic coupling scoop tube position is 0%. | PICFG108A, PICFG108 |  |  |  |  | √ | √ |  |  |  |
| - Select hydraulic coupling as furnace pressure control mode. | PICFG108 |  |  |  |  | √ |  |  |  |  |
| - At DCS, verify all IDF permissive are Satisfied. | Refer to appendices. |  |  |  |  | √ |  |  |  |  |
| - Start IDF at DCS. | F1056 |  |  |  |  | √ |  |  |  |  |
| - Monitor the ff. parameters for the IDF: - Current, amps - Fan bearing temperature, °C - Fan winding temperature, °C - Fan bearing vibration (NDE and DE) - Hydraulic Coupling Furnace Pressure Control at 13% - IDF inlet Damper opening is about 93% | IIF1056 TIFG10562/ TIFG10561 TIFG1056U/ TIFG1056V/ TIFG1056W VIFG10562/ VIFG10561 PICFG108 PIC-FG108A |  |  |  |  | √ √ √ √ √ √ |  |  |  |  |
| - Adjust manually (commonly reduce) the hydraulic coupling furnace pressure controller (PIC-FG108) percentage maintaining furnace pressure of -15mmH2O. (Note: At 16% of Hydraulic Coupling, the IDF Damper Opening is 100%). | PIC-FG108 |  |  |  |  | √ |  |  |  |  |
| - Adjust Primary/Secondary Air Fan Damper Opening to 0%. | FICF A1081 |  |  |  |  | √ |  |  |  |  |

## FAB START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| FAB START UP | F-1055A/ F-1055B |  |  |  |  |  |  |  |  |  |
| - Ensure all valves line up and oil level check are accomplished by AO prior to FAB start. Ensure Filter clean |  |  |  |  |  |  | √ |  |  |  |
| - Ensure Fluidizing Air Damper is at least 25% OPEN, Fluidizing Surge Valve is OPEN and Set to Auto Mode and Discharge Valve is CLOSE and Set to AUTO Mode. | FCVFA1055A1 FCVFA1055B1 |  |  |  |  | √ |  |  |  |  |
| - Ensure Fluidizing Air Blower Suction Isolation Valve is OPEN. |  |  |  |  | √ |  | √ |  |  |  |
| - Ensure All Fluidizing Air Blower Start-up Permissive are satisfied at DCS. | Refer to appendices. |  |  |  |  | √ |  |  |  |  |
| - At DCS, Start Selected Fluidizing Air Blower. | F-1055A/ F-1055B |  |  |  |  | √ |  |  |  |  |
| - Monitor the ff. parameters for the FA blower: - Current: amperes - Bearing temperature: ºC - Winding temperature: ºC - Bearing vibration: mm/s - Air flow: t/hr. | IIF1055A IIF1055A TIFA1055B1 TIFA1055B2 TIFA1055AB1 TIFA1055A2 TIFA1055BU TIFA1055BV TIFA1055BW TIFA1055AU TIFA1055AV TIFA1055AW VIFA1055B1 VIFA1055B2 VIFA1055AB1 VIFA1055A2 FIFA1055 |  |  |  |  | √ √ √ √ |  |  |  |  |
| - Ensure Surge Valve will CLOSE and FAB Discharge Valve will OPEN. |  |  |  |  |  | √ | √ |  |  |  |
| - Increase Fluidizing Air Blower Inlet Damper Opening until Fluidizing air flow increase to 26 T/H | FCVFA1055A1 FCVFA1055B1 |  |  |  |  | √ |  |  |  |  |
| - Set FAB Inlet Damper to AUTO. | FCVFA1055A1 FCVFA1055B1 |  |  |  |  | √ |  |  |  |  |
| - Adjust Secondary Air Fan Damper Opening to 0%. | FICF A1081 |  |  |  |  | √ |  |  |  |  |
| - Set Standby FAB in AUTO Mode. | F-1055A/ F-1055B |  |  |  |  | √ |  |  |  |  |

## SAF START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| SAF START UP | F-1054 |  |  |  |  |  |  |  |  |  |
| - Gradually Close Secondary Air Fan Damper (0%) while monitoring furnace pressure and maintain a negative pressure (-15mmAq). | MCVFA10541 |  |  |  |  |  |  |  |  |  |
| - Ensure all valves line up are accomplished and check oil level by AO prior to SAF start. Ensure filters clean |  |  |  |  |  |  |  |  |  |  |
| - Ensure all valves line up are accomplished by AO prior to SAF start |  |  |  |  |  |  |  |  |  |  |
| - Ensure all Staging Air Damper at Rear and Front Wall Furnace are 10% OPEN. | HICFA105 to HICFA126 |  |  |  |  | √ |  |  |  |  |
| - Ensure all Combustion Air Dampers (MCV-FA1043A/B/C/D) are 25% OPEN. | MCV-FA1043A, MCV-FA1043A, MCV-FA1043B, MCV-FA1043C, MCV-FA1043D |  |  |  |  | √ |  |  |  |  |
| - Ensure all Secondary Air Fan Manual Start Permissive are satisfied at DCS. | Refer to appendices. |  |  |  |  | √ |  |  |  |  |
| - At DCS, Start Secondary Air Fan. Monitor the ff. parameters for the SAF - Current, amps - SAF bearing temperatures, °C - SAF winding temperatures °C - SAF bearing vibration, mm/s | 11F1054 TIFA10542/ TIFA10541 TIFA1054U/ TIFA1054V/ TIFA1054W VIFA10542/ VIFA10541 |  |  |  |  | √ √ √ √ |  |  |  |  |
| - At DCS, Adjust SAF Inlet Damper Manually up until combustion air flow increase to 200T/H (You can use double arrow but be cautious of the furnace pressure reaction). Maintain the furnace pressure of -15mmH2O whilst simultaneously increasing HC Speed of IDF. Target SAF pressure: - > 1200mmH2O = with bed or; - >600 mmH2O = without bed (AH outlet to secondary air pressure transmitter) | FICFA1081 |  |  |  |  | √ |  |  |  |  |

## PAF START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| PAF START UP | F-10531 |  |  |  |  |  |  |  |  |  |
| - Ensure all valves line up are accomplished and check oil level by AO prior to PAF start. Ensure filter clean |  |  |  |  |  |  |  |  |  |  |
| - Verify Cooling Water Pressure for bearing should be 0.5 to 2 kg/cm2. |  |  |  |  |  | √ |  |  |  |  |
| - At DCS, Start Selected Primary Air Fan Lube Oil Pump and set standby Lube Oil Pump to AUTO. |  |  |  |  |  | √ |  |  |  |  |
| - Ensure Biasing Damper of Superheater and Reheater Side are 100% OPEN | HICHR1002A/ HICHR1002B |  |  |  |  | √ |  |  |  |  |
| - Gradually Close Primary Air Fan Damper (0%) while monitoring furnace pressure and maintain a negative pressure (-15mmAq). | FICFA1071 |  |  |  |  | √ |  |  |  |  |
| - Ensure all Primary Air Fan Manual Start Permissive are satisfied at DCS. | Refer to appenndices. |  |  |  |  | √ |  |  |  |  |
| - At DCS, Start Primary Air Fan. Monitor the ff. parameters for the PAF - Current, amps - PAF bearing temperatures, °C - PAF winding temperatures, °C - PAF bearing vibration mm/s | 11F1053 TIFA10532 TIFA10531 TIFA1053U TIFA1053V TIFA1053W VIFA10532/ VIFA10531 |  |  |  |  | √ √ √ √ |  |  |  |  |
| - At DCS, Increase PAF Inlet Damper Manually (Use Single Arrow when adjusting Inlet Damper Opening). Maintain the Furnace pressure to -15mmH2O whilst simultaneously increasing HC Speed of IDF. Target Primary Air Flow: - 180T/H = No Bed - 280 T/H = With Bed | FICFA1071 |  |  |  |  | √ |  |  |  |  |
| - Once the Hydraulic Coupling is at 16% MV and Furnace Pressure is Stable at around -15mmH2O, set the HC Control (Furnace Pressure Control) Mode in AUTO. Adjust the Set value to -15mmH2O (During Auto mode) if needed. |  |  |  |  |  |  |  |  |  |  |

## FURNACE PURGE

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| FURNANCE PURGE |  |  |  |  |  |  |  |  |  |  |
| - Adjust Air Flow to >25% MCR (Furnace Purge Air Flow) by adjusting the inlet vanes of fans and the dampers of secondary air nozzles to permit a purge air flow. - PA fan: Maintain a minimum airflow - Vane for SA fan: required air flow for start-up burner’s air purge. (25%) - Dampers of secondary staging air nozzles close to limit stop (10% OPEN). | FCVFA1055A1/ FCVFA1055B1/ MCV-FA1043A, MCV-FA1043A, MCV-FA1043B, MCV-FA1043C, MCV-FA1043D/ FICFA1071/ MCVFA10541 FICFA1071 FICFA1081 FICFA1043A/ FICFA1043B/ FICFA1043C/ FICFA1043 |  |  |  |  | √ √ √ √ |  |  |  |  |
| - Ensure the following conditions are satisfied at DCS: - Total Air Flow > 25% MCR - Induced Draft Fan is running - Secondary Air Fan is running - Any of Fluidizing blower running - All Coal Feeder Stop - Primary Air Fan is running - All Burner Has no Flame. - All Start-up Burner Oil Valve Close (XV-DO1043-A1/A2/B1/B2/C1/C2/D1/D2) Burner Flame Detector is Off - All Coal Feeder Outlet Isolation valve (XV-CL1061-A7/B7/C7) Close - Limestone Feeder Rotary valve (L-1311) Stop - R/H damper >= 30% Position - S/H Damper >= 60% Position - No Boiler Trip Command - Cyclone Outlet Gas Temperature not H.H. (No Reheater Steam) - Reheater Outlet Header Temp. Not H.H. - Start-up Burner Air Damper in Purge Position (MCV-FA1043-A/B/C/D) at 25% opening. | XV-DO1043-A1/ XV-DO1043-A2/ XV-DO1043-B1/ XV-DO1043-B2/ XV-DO1043-C1/ XV-DO1043-C2/ XV-DO1043-D1/ XV-DO1043-D2 F-1053 XV-CL1061-A7/ XV-CL1061B7/ XV-CL1061C7 L-1311 Refer to appendices. MCV-FA1043-A/ MCV-FA1043-B/ MCV-FA1043-C/ MCV-FA1043-D |  |  |  |  | √ √ √ √ √ √ √ √ √ √ √ √ √ √ √ √ |  |  |  |  |
| - Initiate and Start Furnace Purge for five (5) minutes. |  |  |  |  |  | √ |  |  |  |  |
| - Check MFT will RESET, upon completion of the purge cycle. |  |  |  |  |  | √ |  |  |  |  |
| - Check Biasing Damper will adjust automatically to 30% at Reheater Side and 70% at Superheater side. |  |  |  |  |  | √ |  |  |  |  |
| - Set biasing damper opening to RH 10% and SH 90% |  |  |  |  |  |  |  |  |  |  |
| - Put SH biasing damper to AUTO |  |  |  |  |  |  |  |  |  |  |

## AIR PRE-HEATER SOOT BLOWER START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| AIR PRE-HEATER SOOT BLOWER START UP |  |  |  |  |  |  |  |  |  |  |
| - Ensure Plant Air Compressor is running and compressed air pressure is up to 7 Kg/cm2 |  |  |  |  |  | √ | √ |  |  |  |
| - Check the medium source at LOCAL , OPEN Plant air source and CLOSE steam source |  |  |  |  |  |  |  |  |  |  |
| - Select air heater soot blower source select PLANT AIR at DCS. |  |  |  |  |  | √ |  |  |  |  |
| - Start soot blowing Air Preheater |  |  |  |  |  | √ |  |  |  |  |
| - Set Air heater soot blower Circulation Function to “ON” position at DCS. |  |  |  |  |  | √ |  |  |  |  |

## BURNER START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| BURNER START UP |  |  |  |  |  |  |  |  |  |  |
| - Ensure Diesel Oil pump is running. |  |  |  |  |  | √ |  |  |  |  |
| - Check PCV-DO0002 and PCV-DO1009 is in AUTO MODE. | PCV-DO0002/ PCV-DO1009 |  |  |  |  | √ |  |  |  |  |
| - Check igniter is ready at DCS. | FIC-D01043 |  |  |  |  |  |  |  |  |  |
| - Check Oil Gun is ready at DCS. |  |  |  |  |  |  |  |  |  |  |
| - Press Burner “ON” Push button at DCS. Fire at minimum load. |  |  |  |  |  | √ |  |  |  |  |
| - Check if the igniter extends and sparks. |  |  |  |  |  | √ |  |  |  |  |
| - Check if the oil gun extends. |  |  |  |  |  | √ |  |  |  |  |
| - Check if the shut-off valves for diesel oil supply (XV-DO1043A1/A2) OPENS. | XV-DO1043A1/A2 |  |  |  |  | √ |  |  |  |  |
| - Check if atomizing air valves for burner (XV-DO1043A2) OPENS. | XV-DO1043A2 |  |  |  |  | √ |  |  |  |  |
| - Check if burner lighting off timer counts 90 seconds; if no flame, burner will shut down and purge cycle start. |  |  |  |  |  | √ |  |  |  |  |
| - Adjust FCV-DO1043A3 to adjust diesel oil supply pressure to oil gun. Monitor pressure at PI-DO1043A2. - Oil pressure for burner min = 1kg/cm2 and max = 5kg/cm2. - Oil Flow for Burner min = 614.4 t/hr. and max = 3078 t/hr. | FCV-DO1043A3/ PI-DO1043A2 |  |  |  |  | √ √ |  |  |  |  |
| - Check if flame scanner detects flame. |  |  |  |  |  | √ |  |  |  |  |
| - Check if flame through local sight glass |  |  |  |  |  |  |  |  |  |  |
| - Check if igniter retract. |  |  |  |  |  |  |  |  |  |  |
| - Light off another burner following previous procedure on the diagonal side wall at minimum firing ratio. (IF SUB A START, next to start is SUB D. SUB B/C may start after 30 minutes. |  |  |  |  |  | √ |  |  |  |  |
| - Once all 4 burners are in service, Increase load on all four burners simultaneously to meet start-up curve. Gradient = 1 C/ min |  |  |  |  |  | √ |  |  |  |  |
| - WARMING UP |  |  |  |  |  |  |  |  |  |  |
| - Close all vents and drains of steam side when the Steam drum pressure is 2kg/cm² - Observe steam drum level: swelling approximately > 100° C - Use lowering header drain until to control the level and at steam drum pressure of above 10 Kg/cm² use the MBD and CBD to control the level |  |  |  |  |  |  |  |  |  |  |

## AUXILLIARY WARMING UP

## Note: (May be done simultaneously with Bypass System Warming)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| REQUIREMENT: MS Pressure: >12Kg/cm² MS Temperature: 200-280° C NOTE: Aux Pressure: 10 ksc Aux Temperature: 200 – 350 C Desuperheater SV: 350 C |  |  |  |  |  | √ |  |  |  |  |
| - Gradually OPEN MV AS 1391 | MV AS1391 |  |  |  |  | √ |  |  |  |  |
| - Open Equalizing valve | V-AS1019 V-AS1020 |  |  |  |  |  | √ |  |  |  |
| - Open all drains (V-AS1512, V-AS1513) | V-AS1512 V-AS1513 |  |  |  |  |  | √ |  |  |  |
| - Crack Open PCV AS 1010 to allow line warming |  |  |  |  |  | √ |  |  |  |  |
| - OPEN drains to deaerator and ESP hopper line warming (Monitor Drum Level) |  |  |  |  |  |  |  |  |  |  |
| - When AS and MS temperature are almost equal, increase the opening of PCV AS1010 until it reaches the target pressure and temperature (stable at 10Kg/cm²) | PCV AS 1010 |  |  |  |  |  |  |  |  |  |
| - CLOSE the equalizing line | V-AS1019 V-AS1020 |  |  |  |  |  | √ |  |  |  |

## HP and LP BYPASS SYSTEM WARMING UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Check the permissive to warm the bypass lines. A. Boiler Feed Pump Running |  |  |  |  |  | √ |  |  |  |  |
| - Check the condition of Main Steam Pressure>12KSC | PIMS1002 | >12KSC |  |  |  |  |  |  |  |  |
| - Make sure that Reheat blow-off (MVHR1391) is open. |  |  |  |  |  |  |  |  |  |  |
| - Check all drains at DCS going to flash chamber was in manual and close. - HPBV Drain pot - CR Drain pot (After CRCV) - CR Drain pot (Boiler side) - HR Drain pot - LPBV Drain pot NOTE: Ensure all DP drain to flash chamber shut off valves are CLOSE. Do not use this drain valves as it may cause decay in vacuum during warming up | XV-MS1023 XV-HR1021 XV-HR1022 XV-CR1012 |  |  |  |  | √ |  |  |  |  |
| - Drain all condensates first at Manual drains at Local (SG and TG Side) before opening the HP Bypass Valve | V-MS1513 & 14 V-HR1511 & 12 V-HR1514 & 15 V-CR1515 & 16 |  |  |  |  |  | √ |  |  |  |
| - Crack Open the HP bypass valve PCVMS1020 at 1~3%. Monitor HPBV line temperature must be above saturation temperature to ensure no condensates will form in the piping. | PCVMS1020 | not >3% |  |  |  | √ | √ |  |  |  |
| - Keep Reheater Pressure at 1 – 2 ksc to remove condensate through local drain pot valves. |  |  |  |  |  | √ |  |  |  |  |
| - Close the Manual Drain valves to ditch of the ff. drain pots when pure steam is coming out of the drain. - HPBV Drain pot - CR Drain pot (After CRCV) - CR Drain pot (Boiler side) - HR Drain pot - LPVB Drain pot | V-MS1513 & 14 V-HR1511 & 12 V-HR1514 & 15 V-CR1515 & 16 |  |  |  |  | √ | √ |  |  |  |
| - Keep reheater pressure at 4 ksc to release air through the Reheater Blowoff Valve. |  |  |  |  |  |  |  |  |  |  |
| - Check the Temperature if it is already above saturation temperature. This is to make sure that no condensates will form at the piping at that certain pressure in the bypass lines. Achieve 7.6ksc / 165degC Note: If the Main Steam Temperature is almost equal to the reheat steam temperature or to HP Bypass Outlet Temperature that is the indication that the line is already warmed up. √√(value) | TICR10051 or 52 TIHR10121 or 22 |  |  |  |  | √ |  |  |  |  |

## DEAERATOR WARMING UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Open Auxiliary Steam Supply to Deaerator Valves V-AS1014, PCV-AS1000 and V-AS1013. SV = 1.5 ksc | V-AS1014, PCV-AS1000 and V-AS1013. |  |  |  |  | √ |  |  |  |  |
| - Ensure bypass valve is closed V-AS1015. |  |  |  |  |  |  | √ |  |  |  |
| - Ensure that the water in deaerator storage tank has reached 100ᴼC (TG-CD1104) and Pressure 0.6 MPa (PG-CD1104) | TG-CD1104, PG-CD1104 |  |  |  |  |  | √ |  |  |  |
| - Set PCV-AS10000 to AUTO mode. SV = 1.5 ksc | PCV-AS10000 |  |  |  |  | √ |  |  |  |  |

## FLY ASH TRANSMITTER, ESP RAPPING HAMMER and ESP VIBRATOR

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| FLY ASH TRANSMITTERs |  |  |  |  |  |  |  |  |  |  |
| - Ensure all permissives satisfy |  |  |  |  |  | √ |  |  |  |  |
| - Initiate START to FLY ash Transmitter with coordination to AO | EP5A/B EP4A/B EP3A/B EP2A/B EP1A/B AHA/B/C/D |  |  |  |  | √ | √ |  |  |  |
| - Initiate START to ESP RAPPING motors and vibrator |  |  |  |  |  | √ | √ |  |  |  |

## GLAND SEALING

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| REQUIRMENT: MSP: >12 Kg/cm² AUX steam pressure: >7 Kg/cm² AUX steam temperature: TIAS 1015: at Cold (150-260° C), hot (200-371° C) |  |  |  |  |  |  |  |  |  |  |
| - Initial Condition/Need to Check - Main Steam Pressure | PIMS1002 | >12ksc |  |  |  | √ |  |  |  |  |
| - Aux Steam Pressure | PIAS1004 | >7ksc |  |  |  | √ |  |  |  |  |
| - Gland Steam desuperheater outlet temp | TIAS1015 | 220degC |  |  |  | √ |  |  |  |  |
| - U-seal Established |  |  |  |  |  |  | √ |  |  |  |
| - Vacuum Breaker in Open | MVAV1391 |  |  |  |  | √ |  |  |  |  |
| - TCS Cleared on Permissive |  |  |  |  |  | √ |  |  |  |  |
| - Turbine Running by Turning Gear | TCE350 T1 |  |  |  |  | √ | √ |  |  |  |
| - CEP in service |  | 150T/H |  |  |  |  |  |  |  |  |
| - Open at approx. 10% Inlet Isolation Valve of Gland Steam Exhauster (V-CD1912), maintain pressure at Exhausted Air Press of GSC (PGCD1902) | V-CD1912; PGCD1902 | -0.034ksc |  |  |  |  | √ |  |  |  |
| - Open bypass valve of exhauster line 4 turns open from fully close or approx. 50% open | V-CD1913 |  |  |  |  |  | √ |  |  |  |
| - Put in auto (Gland Steam Separator MVAS1393) and (T/B Gland Steam Drain MVAS1397) at the DCS | MVAS1393&MVAS1397 |  |  |  |  | √ |  |  |  |  |
| - Put in auto the Steam Seal Feed inlet Valve and Gland Steam Exhauster | MVGS1030& TCA680 |  |  |  |  | √ |  |  |  |  |
| - Put in auto the Steam Seal Feed Valve | PV-GS1031 |  |  |  |  | √ |  |  |  |  |
| - Put in auto the Steam Packing Unloading Valve | PV-GS1034 |  |  |  |  | √ |  |  |  |  |
| - Put in auto LP Exhaust Hood Spray | FVCD1904 |  |  |  |  | √ |  |  |  |  |
| - Start Gland Seal Group Control |  |  |  |  |  | √ |  |  |  |  |
| - Refer to the appendices (GLAND SEAL CHART), monitor the valves if the responses are correct. Check on trends also for better monitoring. Stop if there are abnormalities found. | Refer to TCS Appendix Fig. A & B |  |  |  |  | √ |  |  |  |  |

## CONDENSATE POLISHER START UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Select CPP train to be in service - If Train A selected CLOSE train B - If Train B selected CLOSE train A | TRAIN A TRAIN B |  |  |  |  | √ |  |  |  |  |
| - Ensure Anthracite and polisher vents are open |  |  |  |  |  | √ |  |  |  |  |
| - Gradually OPEN MV-CD1007 (OPEN local- 3 % open) - Check CPP outlet pressure - Monitor condensate flow at CPP ( FIQCD1121 – 60t/h) |  |  |  |  |  |  |  | √ |  |  |
| - Ensure valve are in remote and Initiate start to Anthracite filter A and Polisher MB A (if Train A is selected) - Monitor the valves automatically OPEN | MVAV1391 |  |  |  |  | √ |  |  |  |  |
| - CLOSE all vents if water comes out (fully prime) - Monitor FIQCD 1121 flow decrease to 0t/h indicates that the lines are fully prime |  |  |  |  |  | √ |  |  |  |  |
| - Fully OPEN MV-CD1008 (CPP discharge valve) |  |  |  |  |  | √ |  |  |  |  |
| - Ensure pre start check conducted on CPP booster pump - Breaker are ok - Pump fully prime - Inlet valve OPEN - Outlet valve 0% OPEN - Polisher pressure = 24 Kg/cm² |  |  |  |  |  |  |  | √ |  |  |
| - Initiate start to selected CPP booster pump with proper coordination to CRO |  |  |  |  |  |  |  | √ |  |  |
| - Monitor the parameters - Current - Discharge pressure |  |  |  |  |  |  |  |  |  |  |
| - Gradually OPEN the CPP booster pump discharge valve until it reaches the desired pressure = 24Jg/cm² ( around 10% OPEN) |  |  |  |  |  |  |  |  |  |  |
| - Set running CPP booster pump to AUTO |  |  |  |  |  | √ |  |  |  |  |
| - Set standby CPP booster pump to AUTO, discharge valve 10% OPEN and SUCTION valve to 100 % OPEN |  |  |  |  |  |  |  |  |  |  |

## VACUUM UP

Note:  In vacuum-up, we can use Start-up ejector plus the combination of the ff:

| Description | Total No. | COMBINATION |  |  |
| --- | --- | --- | --- | --- |
| 1st Ejector | 2 | 1 | 1 | 2 |
| 2nd Ejector | 2 | 1 | 2 | 2 |

Normal use is only 1 of the 1st ejector and 1 of the 2nd ejector

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Initial Condition - Condenser Air Removal Pre Start-up Checklist has been completed. (Refer to Condenser Air Removal Valve Checklist) (please verify if LPH, HPH Valve included) - Seal Water system in Service |  |  |  |  |  |  | √ |  |  |  |
| - Auxiliary steam pressure is > 10 Kg/cm² |  |  |  |  |  |  |  |  |  |  |
| - Gland Sealing Steps should already finished |  |  |  |  |  | √ |  |  |  |  |
| - Vacuum breaker closed | MVAV1391 |  |  |  |  | √ |  |  |  |  |
| - Sealing Water of Vacuum Breaker need to open | V-MU1020 |  |  |  |  |  | √ |  |  |  |
| - Condensate Flow | FIQCD1120 | 150t/h |  |  |  |  | √ |  |  |  |
| - Confirmed that the Drain valves of the shell of main steam jet air ejector (MSJAE) are open | V-CD1356 (NO), V-CD1354 (NO), V-CD1352 (NO), V-CD1353(NO), V-CD1355(NO), V-CD1351(NO) |  |  |  |  |  | √ |  |  |  |
| - Start Up Ejector (SE) Start - Check sealing water V-AV1315, should be open | V-AV1315 |  |  |  |  |  | √ |  |  |  |
| - CRO open the MV AS1395 | MV AS1395 |  |  |  |  | √ |  |  |  |  |
| - Check and maintain pressure at the header (10.4ksc) | PIAS1004 or 1005 |  |  |  |  | √ |  |  |  |  |
| - Gradually open the (motive steam isolation valve) V-AS1313 Manual valve. Check on the PGAS1006 until it reach 10ksc | V-AS1313&PGAS1006 |  |  |  |  |  | √ |  |  |  |
| - Open the V-AV1314 suction valve | V-AV1314 |  |  |  |  |  | √ |  |  |  |
| - Verify if the valve exhaust hood spray open 100% | FVCD1904 |  |  |  |  | √ |  |  |  |  |
| - Steam Jet Air Ejector(SJAE) Start - Extracted air press reading | PGAS1014 | -0.82ksc (-603mmHg) |  |  |  |  | √ |  |  |  |
| - Counter check on the DCS condenser vacuum reading | PICD1110 | 0.21ksca |  |  |  |  | √ |  |  |  |
| - Check sealing and drains to flash chamber already open | AV1304, AV1305, VCD1356, VCD1354, VCD1352, VCD1353, VCD1355, VCD1351 |  |  |  |  |  | √ |  |  |  |
| - Open the 2nd ejector discharge valve | V-AV1311 or 1310 |  |  |  |  |  | √ |  |  |  |
| - Open the Aux Steam to air ejector Motorized valve | MV-AS1396 |  |  |  |  | √ |  |  |  |  |
| - Open the 2nd ejector motive steam valve | V-AS1304 or 1303 |  |  |  |  |  | √ |  |  |  |
| - Open the 2nd ejector suction valve | V-AV1306 or 1307 |  |  |  |  |  | √ |  |  |  |
| - Open the 1st ejector discharge valve | V-AV1309 or 1308 |  |  |  |  |  | √ |  |  |  |
| - Open the 1st ejector motive steam | V-AS1302 or 1301 |  |  |  |  |  | √ |  |  |  |
| - Open the 1stejector suction valve | V-AV1302 or 1303 |  |  |  |  |  | √ |  |  |  |
| - Check in the gauges if there are abnormalities. Open another set of ejector if necessary | PGAS1012 PGAS1013 PGAS1014 PGAS1007 or PGAS1008 PGAS1009 or PGAS1011 |  |  |  |  |  | √ |  |  |  |
| - Start Up Ejector (SE) Stop - Check if the Extracted air press reading | PGAS1014 | -0.90ksc (-662mmHg) |  |  |  |  | √ |  |  |  |
| - Verify at the DCS the condenser vacuum pressure | PICD1110 | 0.103ksca |  |  |  |  | √ |  |  |  |
| - Close Start-up Air Suction Valve (V-AV1314) | V-AV1314 |  |  |  |  | √ | √ |  |  |  |
| - Gradually Close Motive Steam to Start-Ejector -AS1313 | V-AS1313 |  |  |  |  |  |  |  |  |  |
| - Close the Motorized Valve of Steam to Start-up ejector | MV AS1395 |  |  |  |  |  |  |  |  |  |
| - Vacuum Up Complete. Check if the ff gauges satisfy - Extracted air press | PGAS1014 | -0.962ksc (-707.6mmHg) |  |  |  |  | √ |  |  |  |
| - Verify at the DCS the condenser vacuum press | PICD1110 | 0.05ksca |  |  |  |  |  |  |  |  |
| - Inter-condenser inner press | PGAS1013 | -0.775ksc |  |  |  |  |  |  |  |  |
| - After condenser inner press | PGAS1012 | 0ksc |  |  |  |  |  |  |  |  |
| - 2nd ejector driving steam press | PGAS1007 | 10-11ksc |  |  |  |  |  |  |  |  |
| - 2nd ejector driving steam press | PGAS1008 (only if used) | 10-11ksc |  |  |  |  |  |  |  |  |
| - 1st ejector driving steam press | PGAS1009 | 10-11ksc |  |  |  |  |  |  |  |  |
| - 1st ejector driving steam press | PGAS1011 (only if used) | 10-11ksc |  |  |  |  |  |  |  |  |
| - Inlet Temperature | TGCD1119-1 | 36°C |  |  |  |  |  |  |  |  |
| - Outlet Temperature | TGCD1119-2 | 38.5°C |  |  |  |  |  |  |  |  |

## BED MATERIAL INJECTION (SILICA SAND INJECTION)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| NOTE: BED material injection should be done at 250 °C lower furnace temperature |  |  |  |  |  |  |  |  |  |  |
| - Initiate START to Sand Silo Vent FAN filter |  |  |  |  |  | √ |  |  |  |  |
| - Check Sand injection permissive all satisfied |  |  |  |  |  |  |  |  |  |  |
| - OPEN valve at DCS | XVSD1802A XVSD1802B |  |  |  |  |  |  |  |  |  |
| - Initiate START at DCS |  |  |  |  |  |  |  |  |  |  |
| - Monitor parameters - Dispensing vessel S1300 pressure should be increasing up 3~4Kg/cm², then decrease as conveying air pushes silica sand to boiler injection |  | 4ksc | 5ksc |  |  |  |  |  |  |  |

## BYPASS SYSTEM SERVICING

NOTE: Steam Flow of 40 T/H above is recommended and M/S Pressure of 50 ksc before transfer

| Equipment/Procedure | Tag no. | Operating Limits |  |  |  | Responsible |  |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV |  | CRO | AO | WTP | MH |  |  |
| - Gradually OPEN HP bypass valve to 5% while closely monitoring the ff. parameters. - MS and RH Pressure and Temperature - MS Flow - Drum Level (May cause swelling) - TCV FW1060 DESUP SV 220°C NOTE: HP Bypass Valve Desuperheater Procedure: - Before putting HPBV desup to AUTO, change Set Value to PV Value. - When in AUTO, reduce SV by 15C. - When SV and PV is almost the same, reduce SV again by 15C. - Final SV target = 220C. |  |  |  |  |  |  | √ |  |  |  |  |  |
| - Crack Open LP Bypass valve PCVHR1010 to 1% while closely monitoring Condenser Pressure NOTE: Set the LPBV temp control to AUTO - TCVCD1115 DESUP to 137°C TCV CD 1115 DESUP SV 137° C |  |  |  |  |  |  | √ |  |  |  |  |  |
| - Gradually Increase HP and LP Bypass valve while closing the RH Blow off valve slowly until FULLY CLOSE. Maintain a RH Pressure of 7.5ksc |  |  |  |  |  |  | √ |  |  |  |  |  |
| - After Closing the RH Blow off valve, SET the LPBV PCVHR1001 to AUTO while maintaining pressure of 7.5ksc |  |  |  |  |  |  | √ |  |  |  |  |  |
| - Gradually Close MS Blow off valve to maintain pressure and transfer steam flow to RH steam piping. Closely monitor the RH and condenser pressure. Use HPBV to set the required pressure for turbine steam admission |  |  |  |  |  |  | √ |  |  |  |  |  |
| - Increase the oil firing rate if necessary to reach the required steam pressure and temperature for turbine steam admission (Ex. A-Cold Start-up) - HP Steam Pressure: >57 kg/cm2 - IP Steam Pressure: >7 kg/cm2 - HP Steam Temp: >345 Deg.C - IP Steam Temp: >201 Deg.C |  |  |  |  |  |  | √ |  |  |  |  |  |
| - Manually OPEN the Drain pot to FLASH chamber and monitor the condenser pressure (when condenser pressure is stable set the drain pot to AUTO) |  |  |  |  |  |  | √ |  |  |  |  |  |

## TURBINE INLET WARMING UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV |  | CRO | AO | WTP | MH |  |
| - Turbine Main Steam Motorized isolation valve (MVMS1391) is necessary to be Equalized and OPENED during boiler pressurization at around 20~30ksc of MS Pressure to avoid valve stuck up. It can be serviced simultaneously while servicing the HP and LP Bypass system |  |  |  |  |  |  |  |  |  |  |  |
| - OPEN drain pot DP-MS01 shut off valve going to flash pipe to ensure proper draining of condensate at Turbine Inlet Piping | XVMS1011 |  |  |  |  |  | √ |  |  |  |  |
| - Gradually OPEN turbine inlet equalizing motorized valve until fully OPEN while closely monitoring the following: - Steam Drum Level (May cause swelling due to transfer of steam flow) - Main steam pressure and flow - Turbine inlet steam temperature | MVMS1392 |  |  |  |  |  | √ |  |  |  |  |
| - It may take time to equalize steam pressure and temperature before and after the Turbine Inlet Equalizing valve (Around 5 to 10 minutes). Closely monitor saturation temperature of steam to prevent hammering of turbine inlet piping |  |  |  |  |  |  | √ |  |  |  |  |

## PREPARATION FOR STARTING AND WARMING UP OF TURBINE

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Check that the emergency trip device is in the tripped position |  |  |  |  |  | √ |  |  |  |  |
| - Check that all turbine main steam valves are closed. Note: This assures that no steam admission valves are inadvertently opened when the operating oil pressure is established, and verifies the closed position of these devices for subsequent procedural steps. |  |  |  |  |  | √ |  |  |  |  |
| - Turn the emergency oil pump test valve to test position at main oil tank console box. |  |  |  |  |  |  |  |  |  |  |
| - Check that the emergency oil pump starts automatically and operates satisfactorily. | 1P1923 |  |  |  |  | √ |  |  |  |  |
| - When the emergency oil pump starts, it is probable that the turning gear may stop because of bearing oil pressure dip sensed by the turning gear interlock when starting pump. | 1P1923, TCE350T1 |  |  |  |  | √ |  |  |  |  |
| - Check if the turbine shaft stopped. |  |  |  |  |  |  |  |  |  |  |
| - Restart and engage the turning gear, if it has stopped, and proceed to the next step. |  |  |  |  |  |  |  |  |  |  |
| - Stop the emergency oil pump and confirm following items. - Main oil pump is running. - Bearing oil pressure is more than. - Turbine shaft is still rotating. | 1P1923 1P1922A & | >1.05kg/cm2g |  |  |  |  |  |  |  |  |

## ATS AUTO EXECUTE

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Initial condition - Bypassed system already established - ANN Reset and acknowledge all alarms - Gland sealing and vacuum is established | PCVMS1020 & PCVHR1010 TCE050_1 |  |  |  |  | √ √ |  |  |  |  |
| - All Drain Valves must be Open and Auto E. G. (1MVST1002A) MSV(A) Abv seat sec drain valve > Open > Execute > Auto > Execute - MSV A Above Seat Drain Valve - MSV B Above Seat Drain Valve - CV A Above Seat Drain Valve - CV B Above Seat Drain Valve - CV B Below Seat Drain Valve - CRV A Below Seat Drain Valve - CRV B Below Seat Drain Valve Note: Turbine drain system consists of the following: - Main and reheat steam piping - Extraction steam line drains - Permanent orifice drains which are provided on the gland steam header All main steam piping between the boiler and main stop valves should be thoroughly blow down and pre-warmed. This should be done with main steam and hot reheat piping drains primarily. This procedure is necessary to avoid and protect against the possibility of erosion on valve stems, valve seats and nozzles. The temperature of steam should be sufficiently high to prevent throttling into the wet region. All drains beyond the main stop valve, located in the steam piping should be opened to condenser. (need to review if need to remove) | 1MVST1002A, 1MVST1002B, 1MVST1004A, 1MVST1004B, 1MVST1008, 1MVST1010A, 1MVST1010B, |  |  |  |  | √ |  |  |  |  |
| - Put all equipment and valves in AUTO under Function Group AUXILIARY CONTROL: (at TCS) - Lube Oil - Control Oil Turning - Steam Valve (MSV, CV) - Non Return Valves - Gland Seal (Verify again) | Go to AUX CONTROL/ |  |  |  |  | √ |  |  |  |  |
| - ATS Auto Execute Note: - When the operator selects “ATS AUTO MODE” from TCS, ATS program will start to monitor the CRITERIA (refer on appendices ATS CRITERIA). - List of criteria is also shown in TCS by CRITERIA FULFILLED > (LOOK FOR CRITERIA DETAILS DISPLAY) CRI NO 1. 1 TO CRI NO. 3.1. When the criteria are NOT fulfilled, RED INDICATION will be shown in the CRITERIA NO. BOX OF THE TCS display. - When the operator selects “OFF MODE” PB from TCS, ATS program will automatically stop. - When the MAJOR TROUBLE occurs in steam turbine/generator/TCS which will result to TURBINE TRIP COMMAND, ATS program automatically changes the “ATS AUTO” mode to “OFF” mode(e.g. Major Trouble: Power supply trouble – Power Off) | TCA501_1 |  |  |  |  | √ |  |  |  |  |
| - Check each criteria(refer on appendices ATS CRITERIA). |  |  |  |  |  | √ |  |  |  |  |

Note: After ATS Auto Execute (On) and all the criteria has been checked, ATS sequence can be started by clicking manually

TCS will automatically select the turbine start-up mode which is the ff:

- AMBIENT

- COLD

- COLD 1

- COLD 2

- WARM

- HOT

ATS START-UP SEQUENCE

- HP TURBINE WARMING

- TURBINE PREPARATION

- TURBINE RUB CHECK

- ACCELERATION

- EXCITATION

- SYNCH. & INITIAL LOAD

- LOAD UP

- NORMAL OPERATION

Note: Operator can skip step 1-3 at Cold 2, Warm & Hot Start-up mode

List of the Criteria for every step during turbine start up (ATS criteria table for IP start up mode)

- CRITERIA GROUP An – CRITERIAGROUP OF PRESMISSIVE CONDITION TO PERMIT THE STEP-IN

- CRITERIA GROUP Bn – CRITERIAGROUP OF MONITOR CONDITIONS TO MONITOR THE WHOLE STEP DURING EXECUTION

- CRITERIA GROUP Dn – CRITERIAGROUP OF COMPLETION CONDITIONS TO FINISH THE EXECUTING STEP

(Refer to Criteria List on the Appendices)

When the operator selects the present or upper level step from the TCS, the step control program starts to execute the present step only if the step-in condition (CRITERIA A) of the present step is satisfied. During the present step execution, the step control program keeps monitoring the step monitoring condition (CRITERIA B) of the present step. When an abnormal situation causes the step monitoring condition unsatisfied during the present step execution, the step control program correspondingly suspends the step execution.

List of Troubles for Criteria on Hold

- Vibration high (1.24)

- Diff expansion high (1.28)

- Exhaust hood temp high (1.12)

- Condenser vacuum low (1.11)

- Bearing oil press low (1.15)

- Thermal stress high

## START HP TURBINE WARMING

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| Note: The most effective means of accomplishing this pre-warming is causing pressurization, the HP turbine with steam, thus raising the temperature to the saturation temperature of the steam or higher. The pressure normally specified is 4.0kg/ cm2g to 5.0kg/cm2g. The pressurization should be used whenever the first stage shell inner surface is below 150°C. For higher metal temperature, the pre-warming is not necessary. NOTE: Gland Seal and Vacuum must be established - Check of the ff: - MSP | TIMS10041 | >12ksc |  |  |  | √ |  |  |  |  |
| - RHT | PIMS1002 | 175-260ksc |  |  |  | √ |  |  |  |  |
| - RHP | PICHR1003 | >5ksc |  |  |  | √ |  |  |  |  |
| - HPBV and LPBV is in service (Check Steam quality refer to HITACHI recommendation) | PCV1020 & PCVHR1010 |  |  |  |  | √ |  |  |  |  |
| - Check Gov/LLM Select - AFR>Gov/LLM Select >Gov> execute | TCE172_1 |  |  |  |  | √ |  |  |  |  |
| - Verify Load Limit Set | TCE205_A1 | -2% |  |  |  | √ |  |  |  |  |
| - Verify Governor Set | TCE196_A1 | 0% |  |  |  | √ |  |  |  |  |
| - Check the condition for HP Turbine Pre-warming - Check the turning gear operation. | TCE143_A1_PV | 3rpm |  |  |  | √ |  |  |  |  |
| - Check the auxiliary steam pressure | PIAS1004 or 05 | >7.0 kg/cm2g |  |  |  | √ |  |  |  |  |
| - Check that the cold reheat drain valve after and before cold reheat check valve are fully opened. | XVCR1011 & 12 |  |  |  |  | √ | √ |  |  |  |
| - Check that the pressure in condenser | PICD1110 | <0.14 kg/cm2g |  |  |  | √ |  |  |  |  |
| - Check the indication “TURBINE TRIPPED”. |  |  |  |  |  | √ |  |  |  |  |
| - Check that the Auxiliary Steam temperature | PIAS1004/05 | 200 to 267°C |  |  |  | √ |  |  |  |  |
| - Check CV (B) Below Secondary Drain Valve in Auto | MVST1008 |  |  |  |  | √ |  |  |  |  |
| - HPT Warming Line Drain Valve in Auto | MVAS1394 |  |  |  |  | √ |  |  |  |  |
| - Put HPT-Warming Valve in Auto | MVAS1011 |  |  |  |  | √ |  |  |  |  |
| - Ensure Ventilator Valve (VV) is closed. | FVCR1902 |  |  |  |  | √ |  |  |  |  |
| - Click HP Turbine Warming >Exec |  |  |  |  |  | √ |  |  |  |  |
| - Monitor the operation of the valves. (this automatically done by the TCS) Refer to the appendices HP Turbine Warming Chart. - TCS will fully open HP turbine warming line drain valve MVAS1394 and will hold it for one minute. Then will close it. | MVAS1394 | (refer to the chart in the appendices) |  |  |  | √ |  |  |  |  |
| - TCS will Open HP Turbine warming Valve (MV-AS1011) Note: Maximum position at initial opening of the valve is 40-42% opening | (MV-AS1011) |  |  |  |  | √ |  |  |  |  |
| - TCS will Close CV (B) below seat drain valve from 100% to 20% opening after the 30s that the AS1011 reached the opening of 10% | MVST1008 |  |  |  |  | √ |  |  |  |  |
| - Check the turning gear disengages. Note: - During HP turbine warming, steam goes from HP to ILP through Packing No. 2 thus, turbine speed increases. Take note of increase in rpm. Recommended turbine speed during HP turbine warming is 200 rpm. Monitor maximum speed reached | TCE350T1 |  |  |  |  | √ |  |  |  |  |
| - Check that ventilator valve is fully closed. By this operation, warming steam flows into HP turbine from auxiliary steam line through the HP turbine warming valve | FVCR1902 |  |  |  |  | √ |  |  |  |  |
| - Notice the position of the HP turbine warming valve reduce to 5% if the HP exhaust pressure reach 5ksc, and open to 40% max if the pressure drop to 4ksc. (refer to the diagram) Note: - When HP Turbine Metal Temperature reaches at 150°C. The holding operation should be carried out. See FIGURE 2 for the required holding time. - During pre-warming operation, metal temperature should be increased at a rate not greater than that indicated in allowable metal temperature differential in Section 7 | MV-AS1011 |  |  |  |  | √ |  |  |  |  |
| - Check if it will close the cold reheat drain upstream non-return valve. (for verification again during start-up) | LVCR1011/12 |  |  |  |  | √ | √ |  |  |  |
| - Warming Operation Complete. Notice the ff: - TCS will Open CV (B) below seat drain valve. | MVST1008 |  |  |  |  | √ |  |  |  |  |
| - TCS will Close HP Turbine Warming Valve. | MV-AS1011 |  |  |  |  | √ |  |  |  |  |
| - TCS will fully Open Ventilator Valve (FV-CR1902) when HP Turbine Warming valve is fully closed. | FV-CR1902 |  |  |  |  | √ |  |  |  |  |
| - HP turbine internal pressure is back to normal (vacuum condition) | PICD1110 |  |  |  |  | √ |  |  |  |  |
| - Eccentricity of 0.06 mm is noticeable after turning gear engaged. Wait for one to two minutes until eccentricity reaches its normal value of 0.02 to 0.03 mm at turbine speed of 3 rpm. | 1ZEST1004 |  |  |  |  | √ |  |  |  |  |
| - Check if it will open the cold reheat drain upstream non-return valve. (for verification again during start-up) | LVCR1011/12 |  |  |  |  | √ | √ |  |  |  |

## SERVICE MS & RH FOR TEMPERATURE CONTROL

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| MS DESUP = > 46 MSF RH DESUP = > 69MSF NOTE: Transfer operation complete |  |  |  |  |  |  |  |  |  |  |
| Control MST and RHT by servicing MS and RH Desuperheater (refer to TG start up curve for the target temperature |  |  |  |  |  |  |  |  |  |  |
| MS desuperheater can put to AUTO, set SV according to START-UP CURVE |  |  |  |  |  |  |  |  |  |  |
| Set biasing damper and RH to Remote- Auto when RHT-PV is almost equal to R-SV |  |  |  |  |  |  |  |  |  |  |

## START TURBINE PREPARATION- CHEST WARMING (holding time: 60mins)

Also refer to ATS CRITERIA (note: MSV and CV above seat drain valves OPEN)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| Note: When CV Chest inner or outer wall temperature is 150°C or less, CV Chest Warming by using main steam is required before turbine rolling - Check on the TCS, CHEST WARMING REQUIRED | 1TEST1904B1_PV |  |  |  |  | √ |  |  |  |  |
| - Turbine Preparation>Execute | TCA521_1 |  |  |  |  | √ |  |  |  |  |
| - Check the Turbine Reset automatically and GOV and not the load limiter (LLM) is not operating. Master trip solenoid valves are energized. | TCE114_1 TCE205_A1 |  |  |  |  | √ |  |  |  |  |
| - Check that the RSV A & B Open to 100%. Inform boiler side. | 1ZTST1905AB & BB |  |  |  |  | √ |  |  |  |  |
| - Check that the standby COP will run also due to pressure drop. Stop the running standby if the pressure stabilizes. E.G. COP(B) > MANUAL > EXECUTE > STOP. THEN SET IT TO AUTO AT COP PRESSURE >160KSC BY: COP(B) > AUTO > EXECUTE (COP A RUNNING) | 1P1931A or B |  |  |  |  | √ |  |  |  |  |
| - Check Steam Pressure Permissive for Turbine Reset. Refer to the table on the appendices (Permissive Condition for Reset) |  |  |  |  |  | √ |  |  |  |  |
| - Check if CV(B) crack open before the MSV open | 1ZTST1904B |  |  |  |  | √ |  |  |  |  |
| - Check that MSVs open (by internal bypass) to warming position. (min and max 0-3% opening) Refer to the appendices (Chest Warming Chart) Note: - Monitor the differential temperature between CV chest inner and outer metal surface. When it rises more than 90ﾟC, TCS will close MSV. - Monitor the differential temperature between CV chest inner and outer metal surface. When it lowers less than 80ﾟC, TCS will reopen MSVs to warming position. | 1ZTST1903A & B |  |  |  |  | √ |  |  |  |  |
| - After turbine reset, annunciator alarms due to automatic opening of non-return valves. Acknowledge by Auxiliary Control > Non-return Valves > Test > Reset > Execute (#1, #2, #3, #4, #5). It shows abnormal display (calibrated location of limit switch) Note: If after two tries of RESET but NRV is still in abnormal state, check LOCAL site for troubleshooting. Probable cause could be the air supply for solenoid valve is closed. (Because the main steam does not come into the HP-turbine, the NRV should be open in close position) |  |  |  |  |  | √ |  |  |  |  |
| - Auxiliary Control > Drain Valves > Open 7 drain valves > set seven drain valves in Auto | AUX CONTROL / DRAIN VALVE |  |  |  |  | √ |  |  |  |  |
| - CV chest warming is complete when: - CV Outer Wall Temp. ≥180 ℃& CV Inner and Outer Metal ∆T ≤50 ℃. - OR CV Chest warming has been carried out of minimum of 1hr |  |  |  |  |  | √ |  |  |  |  |
| - After chest warming is completed, check if MSVs open at 100% position. RSV 100% Open, CVs=0%, ICVs=0% Note: - Even if Criteria Dn is satisfied, do NOT proceed to RUB CHECK until ALL (MS and RH) STEAM TEMPERATURE MISMATCH IS WITHIN RANGE. Verify at CRITERIA DETAIL DISPLAY (1/4). - Reheat Steam Temperature should be at 205 °C. | 1ZTST1903A & B 1ZST1905AB & BB |  |  |  |  | √ |  |  |  |  |
| - Check ats criteria, no error or red lamps on the display Note: Load limit (102%) and governor (0%) automatically set by the tcs in turbine preparation for rolling |  |  |  |  |  | √ |  |  |  |  |

## START TURBINE RUB CHECK

FOR COLD 2- WARM and HOT START-UP at ATS, TURBINE RUBE CHECK can be bypassed

Refer to (XII APPENDICES –START UP CURVE per MODE)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| For COLD START-UP: MS: 60Kg/cm² = 400°C= > 30t/h RH: 7.5Kg/cm² = 415°C |  |  |  |  |  |  |  |  |  |  |
| Note: Before the start of turbine rolling, 3 conditions must be satisfied (Check the graph on appendices) For Warm and Hot Start at ats auto, turbine rub check can be bypassed - Initial Condition - Turbine Warming Completed |  |  |  |  |  | √ |  |  |  |  |
| - Allowable temperature of main steam on turbine metal(refer to HP and IP Steam Permissive Chart on the appendices) | MONITOR/ CASING METAL |  |  |  |  | √ |  |  |  |  |
| - Allowable Reheat steam temperature on turbine metal (refer to HP and IP Steam Permissive Chart on the appendices) Note: Monitor MSV Inlet Steam Temp VS HP After first stage Inner Wall Metal Temp and CRV inlet steam temp. vs. reheat bowl inner metal temp. Make Sure to be always on inside the region so that turbine will be heated accordingly by its steam supply. Always monitor the temperature of the turbine and always inform boiler operator to maintain on the desired temp of the steam supply for the steam condition. | MONITOR/ CASING METAL |  |  |  |  | √ |  |  |  |  |
| - Check ATS Criteria (verify if no criteria miss before proceed) |  |  |  |  |  | √ |  |  |  |  |
| - Rub Check> execute | TCA522_1 |  |  |  |  | √ |  |  |  |  |
| - Check if ATS will Select target speed 200 rpm for rub check. | TCE168_A1 |  |  |  |  | √ |  |  |  |  |
| - Check if ATS acceleration rate (verify on the chart depends on start mode) refer to appendices STARTING CHART TO RATED SPEED AND LOADING-UP | TCE168_A2 |  |  |  |  | √ |  |  |  |  |
| - Check if ICVs open. Monitor valve position. | 1ZTST1905AA & BA |  |  |  |  | √ |  |  |  |  |
| - At >4rpm, check that the turning gear disengages and its motor is stopped automatically. | TCE350T1, TCE143_A1 |  |  |  |  | √ |  |  |  |  |
| - Monitor when the speed reaches approx. 200 r/min, ATS automatically set “ICV to CLOSE” to keep the speed from rising too fast. | 1ZTST1905AA & BA |  |  |  |  | √ |  |  |  |  |
| - Aux Operator to check if there is rubbing in the turbine field area. Monitor bearing vibration and temperature at tcs. Note: Listen carefully for rubs or abnormal sound in the turbine and generator interior, vibration at each bearing pedestal and vibration on the shaft. When Turbine Speed coast down below 100rpm, rub check is completed. | MONITOR/ TSI |  |  |  |  |  | √ |  |  |  |

## START ACCELERATION

| MODE | PRESSURE (Kg/cm²) |  | TEMPERATURE (°C) |  | FLOW (t/h) |
| --- | --- | --- | --- | --- | --- |
|  | MS | RH | MS | RH | MSF |
| Ambient cold | 61.2 | 8.5 | 400 | 415 | >40 |
| Cold 1 | 61.2 | 8.5 | 400 | 415 | >40 |
| Cold 2 | 61.2 | 8.5 | 400 | 415 | >60 |
| Warm | 81.6 | 8.5 | 400 | 415 | >80 |
| Hot | 110 | 8.5 | 455 | 485 | >120 |

TURBINE ROLLING AND HEAT SOAKING

| START-UP MODE | ACCELERATION RATE | 1800rpm (holding time in minutes) | 3600rpm (holding time in minutes) |
| --- | --- | --- | --- |
| Ambient cold | 120 rpm/m | 88 | 86 |
| Cold 1 | 120 rpm/m | 58 | 55 |
| Cold 2 | 120 rpm/m | 30 | 25 |
| Warm | 180 rpm/m | 0 | 22 |
| Hot | 360 rpm/m | 0 | 0 |

HP AND IP STEAM PERMISSIVE CHART

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Initial Condition, Rub check completed or Rub check has been bypassed because of Warm or Hot Start | TCA754_1 & TCA522_1 |  |  |  |  | √ |  |  |  |  |
| - Select Acceleration>Execute. TCS will select the acceleration rate and heat soaking (refer to the attached Heat Soaking Graph in the appendices, ATS will calculate automatically) | TCA523_1 |  |  |  |  | √ |  |  |  |  |
| - Check that the HP cylinder ventilator valve, confirmed if fully opened. | FVCR1902 |  |  |  |  | √ |  |  |  |  |
| - TCS will increase the turbine speed. The CV open until the speed reaches 400 r/min. Opening of the control valve at 400 rpm is locked by TCS. Monitor % opening of CVs when turbine speed of 400 rpm is reached. Turbine is heat soaked at 400 rpm (depend on the start-up mode) - CV (A) – app. 10% open - CV (B) – app. 3% open | 1ZTST1904A & B |  |  |  |  | √ |  |  |  |  |
| - Check that the ICV will open and the turbine speed over 400 r/min | 1ZTST1905AA & BA |  |  |  |  | √ |  |  |  |  |
| - ATS automatically select the target speed 1,800 r/min. | TCE168_A1 |  |  |  |  | √ |  |  |  |  |
| - Monitor % opening of ICVs until turbine speed of 1 800 rpm is reached. | 1ZTST1905AA or AB |  |  |  |  | √ |  |  |  |  |
| - Open SPEED LOAD/HOLD, while monitoring the vibration at trend no. 9 and 11. CRITICAL ZONE is highlighted at 1 372 to 1 723 rpm. At critical zone, Speed Load HOLD could NOT be held. Turbine should be increased steadily through a critical speed. The turbine cannot hold at critical speed bands by the TCS program. Observed and press HOLD for abnormal sound and vibration. Note: - The operator can manually select the “HOLD ON” PB to hold the present turbine speed/load. - When abnormal states of turbines are restored, ATS program flickers the “HOLD OFF” PB on TCS HMI. The operator can manually operate the “HOLD OFF” PB to continue executing the present step. - The turbine speed/load cannot be held manually/automatically held under the following turbine states: - Turbine speed is in the critical speed band during “ÄCCELERATION” step execution because ATS keeps increasing turbine speed to get out of critical band (for turbine protection). - Turbine control is in the transfer region from ICV to CV during “LOAD UP” step execution because ATS program keeps performing the ICV to CV transfer (for turbine protection). - Turbine vibration at 1800rpm heat soaking still increases. This is normal. And when the turbine accelerates from 1800rpm to 3600rpm, vibration of the turbine decreases. Program automatically hold the turbine speed/load under ff. Turbine states: - Vibration high (outside of the “turbine speed critical zone”) - Diff expansion high - Exhaust hood temp high - Condenser vacuum low - Bearing oil press low - Thermal stress high | TCE164_1 |  |  |  |  | √ |  |  |  |  |
| - After 1800rpm elapsed time. Check HP first stage inner wall metal temp >170°C | 1TEST10011 | >170°C |  |  |  | √ |  |  |  |  |
| - After 1800rpm elapsed time. Check the shell expansion if >3mm | 1ZEST1001 |  |  |  |  | √ |  |  |  |  |
| - When the heat soak operation at 1,800 r/min is completed, check if ATS will select the target speed 3,600 r/min and acceleration rate automatically. Refer to the appendices for the heat soaking time. | TCE168_A1 TCA168_A5 |  |  |  |  | √ |  |  |  |  |
| - Observe the followings when coming up to speed - Metal temperature thermocouples: - MSV inner wall metal temperature - MSV outer wall metal temperature - CV chest inner wall metal temperature - CV chest outer wall metal temperature - HP turbine first stage inner wall metal temperature - HP turbine first stage outer wall metal temperature - Reheat bowl inner wall metal temperature - Reheat bowl outer wall metal temperature - Temperature differences between inner and outer / upper and lower surfaces and temperature gradient should be minimized and held below the allowable limits described in Section 7 - Shell and differential expansion: Shell and differential expansion can be checked by the following indications. - Turbine differential expansion(LP) - Turbine shell expansion(HP) Note: When coming up in speed, variations in differential expansion are to be expected. The rotor does not usually go short upon starting. The rotor will go long if it is being heated more rapidly than the shell. If the indication approaches the red band, the trend may be reversed by lowering steam temperature, speed, or unloading the unit. If the indication of the IP / LP turbine goes into the red band, shut down the unit at once and allow temperatures to equalize on turning gear. | 1TEST1903B1 1TEST1903B2 1TEST1904B1 1TEST1904B2 1TEST10011 1TEST10012 1TEST10041/42 1TEST1005 1ZEST1002 1ZEST1001 |  |  |  |  | √ |  |  |  |  |
| - Listen for rubbing noise. If serious rubbing develops, shut the unit down and investigate the cause. |  |  |  |  |  |  | √ |  |  |  |
| - Check Vacuum: With correct vacuum and normal operating procedure, the LP turbine exhaust hood temperature should not exceed 80°C before synchronizing. Check the LP turbine exhaust hood temperature. | PICD1110 TIST11101 02 or 03 |  |  |  |  | √ |  |  |  |  |
| - Check bearing oil temperature: Allow oil temperature of the bearings to increase with speed. Check if oil temperature of the bearings reached at least 40°C until synchronized. Make sure that the set point of turbine lube oil temperature is 46°C at rated speed. Normal operating oil inlet temperature is specified in limitation items of steam turbine operation in Section | 1TELO1001_PV |  |  |  |  | √ |  |  |  |  |
| - Check that the bearing oil pressure is normal and the green lamps go on. |  |  |  |  |  | √ |  |  |  |  |
| - When the heat soak operation at 3,600 r/min is completed, check that: - CVs will be fully closed. (Will be closed in about 5 min.) | 1ZTST1904A & B |  |  |  |  | √ |  |  |  |  |
| - Ventilator valve is fully opened. | FVCR1902 |  |  |  |  | √ |  |  |  |  |
| - ICVs remain in its final % opening | 1ZTST1905AA & BA |  |  |  |  | √ |  |  |  |  |
| - When the step satisfies “criteria d”, the control program correspondingly finishes the present step (e.g. “HP turbine warming”) execution. Wait for 120 sec timer after heat soak elapsed in order to clear the criteria D. |  |  |  |  |  | √ |  |  |  |  |

## START GENERATOR EXCITATION

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Check AVR if in service and in Auto | TCA587_2 |  |  |  |  |  | √ |  |  |  |
| - Push the “excitation” control start button. (Make sure the reheated steam pressure is between 7.0-8.5 kg/cm2) EXCITATION > SELECT > EXECUTE | 1PTHR1901_PV TCA524_1 |  |  |  |  | √ |  |  |  |  |
| - During turbine excitation, Check the ff: - Field CB (41) closed - Generator voltage to 13.8kV | TCA587_1 TCA310_A2_PV TCA312A2_PV TCA314A1_PV |  |  |  |  | √ |  |  |  |  |
| - Check excitation criteria completed |  |  |  |  |  | √ |  |  |  |  |

## SYNCHRONIZATION

Option 1: TCS will give command for automatic synchronization (ASD)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Verify the following before synchronizing: LP Turbine Exhaust Hood not > 80°C - Bearing Oil temperature at least 40°C - Turbine Lube Oil Tem is 46°C at rated speed. - Bearing Oil Pressure at Normal and the GREEN lamps go ON. | 1TELO1001_PV |  |  |  |  | √ |  |  |  |  |
| - At synchronizing panel, execute the following: - 52G – select - Operation selection – remote - Synch mode - Auto for tcs control | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - At TCS click SYNCH INITIAL LOAD > SELECT > EXCECUTE | TCA525_1 |  |  |  |  | √ |  |  |  |  |
| - After the generator is synchronized, check that the red lamp of the generator circuit breaker (52G) goes on. |  |  |  |  |  | √ |  |  |  |  |
| - Verify if the space heater both for Gen and AC Exciter was open after 52G Closed | TURBINE CONTROL / GEN/EXCITER/ SPACE HEATER |  |  |  |  | √ | √ |  |  |  |

Option 2: Automatic synchronization using the SYN (Operating Console for Synchronizing)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Check. Ready to Synchro light should lit if all of the ff: satisfied - 41 Closed and voltage of the Generator established to 13.8Kv - 52L Closed - no trip in the Generator protection - no trip in the Generator Transformer and Unit Transformer Protection | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Selector to 52G | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Operation to SYN | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Synchronizing operation mode to Man | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Press Auto SYN Start | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Adjust the voltage and frequency to be nearly the same on the Grid | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Synchronizing operation mode to OFF | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Synchronizing operation mode to AUTO | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Press Auto SYN Start | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Let the controller for auto synchronization. Synchronize complete if 52G Circuit breaker closed. | SYN PANEL |  |  |  |  | √ |  |  |  |  |
| - Verify if the space heater both for Gen and AC Exciter was open after 52G Closed | TURBINE CONTROL / GEN/EXCITER/ SPACE HEATER |  |  |  |  | √ |  |  |  |  |

Note:

- The turbine speed matches with the synchronizing speed automatically.

- Synchro scope clockwise direction – generator output voltage/frequency > grid voltage/frequency

- Synchro scope counter clockwise direction – grid voltage/frequency > generator output voltage/frequency

- During auto synch mode by the tcs, generator voltage and frequency (incoming) automatically adjusted higher to the grid voltage and frequency (running) to prevent back feeding.

- Lower difference in voltage and frequency will be observed by slow rotation of the synchro scope to the clockwise direction

At 12 o’ clock position, 52G will be closed (unit synch) which supply initial load and during ats, gen. Initial load automatically set the initial load base on the start-up mode of the steam turbine

## INITIAL LOAD

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Verify initial load based on metal temperature of steam turbine. Initial load in MW based on start-up mode in the steam turbine - Ambient cold – 4.5 mw, 45 minutes holding time - Cold 1 – 4.5 MW, 45 minutes holding time - Cold 2 – 4.5 MW, 45 minutes holding time - Warm – 4.5 MW, 45 minutes holding time - Warm – 4.5 MW , 15 mins instead of 45 Mins - Hot – 7.5MW, no holding time | TCE194_A1 Or TCE070A1_PV |  |  |  |  | √ |  |  |  |  |
| - Verify initial load holding time based on metal temperature of steam turbine. Refer to the graph in the appendices | TCA586_A5 |  |  |  |  | √ |  |  |  |  |
| - Check for operational status. Monitor the steam temperature and shell metal thermocouples very carefully because rapid temperature changes occur at this time. The turbine metal temperatures can be monitored on the TCS. | MONITOR/CASING METAL |  |  |  |  | √ |  |  |  |  |
| - Maintain the initial load until the LP turbine exhaust hood cools down below 52°C. Check the LP turbine exhaust hood temperatures. | 1TEST1110_PV |  |  |  |  | √ |  |  |  |  |

## LOAD – UP

| MODE | PRESSURE (Kg/cm²) |  | TEMPERATURE (°C) |  | FLOW (t/h) |
| --- | --- | --- | --- | --- | --- |
|  | MS | RH | MS | RH | MSF |
| Ambient cold | 61.2 | 8.5 | 400 | 415 | >80 |
| Cold 1 | 61.2 | 8.5 | 400 | 415 | >80 |
| Cold 2 | 61.2 | 8.5 | 400 | 415 | >80 |
| Warm | 81.6 | 8.5 | 400 | 415 | >80 |
| Hot | 110 | 8.5 | 455 | 485 | >120 |

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| Note: - Upon synchronization, load will automatically increase to initial load of 4.5MW. Maintain initial load until the LP turbine exhaust hood cools down below 52°C. - When the selector button of the LP turbine exhaust hood spray water control is in AUTO position, the spray is operated automatically when load is <15% of rated load. - Increase ICV opening, while LPBV reduces its opening to maintain reheat steam pressure along with the increase of the steam flow to ILP turbine. - Call the WTP before Load up (for chemical adjustment) |  |  |  |  |  | √ |  | √ |  |  |
| - Remote LP and HP Bypassed Valve | PCVMS1020 & PCVHR1010 |  |  |  |  | √ |  |  |  |  |
| - When initial load holding is completed, AT TCS, LOAD UP > SELECT > EXECUTE | TCA526_1 |  |  |  |  |  |  |  |  |  |
| - Increase the load by rate of 5 %/min until HP & LP bypass valve is fully closed or reaches to 20 MW. Within this operation, intercept valves are fully opened and CVs are opened to control the turbine load. | TCA526_1 PCVMS1020 & PCVHR1010 |  |  |  |  | √ |  |  |  |  |
| - Check that the cold reheat non-return valve is opened if CVs begin to open. | 1XVCR1901AF |  |  |  |  | √ |  |  |  |  |
| - Check that the ventilator valve is closed if the turbine control valves begin to open | 1FVCR1902 |  |  |  |  | √ |  |  |  |  |
| - At load = 20 MW OR HPBV is fully closed, verify if Transfer Operation (T/R) is completed. | TURBINE CONTROL/ UNIT CONTROL / TRASFER REGION COMPLETE |  |  |  |  | √ |  |  |  |  |
| - If T/R is completed, select AFR> AFR SELECT> SET > EXEC to switch from Gov to LLM | TCE170_1 TCE172_1 |  |  |  |  | √ |  |  |  |  |
| - Monitor trend of LLM. | TCE205_A1 |  |  |  |  | √ |  |  |  |  |
| - When LLM is already stable from decreasing (shown by a straight line), immediately select AFR >Gov/LLM Select >LLM >EXEC NOTE: Load CANNOT be decreased after transfer operation. CV may fully close if load is decreased. | TCE205_A1 TCE172_1 |  |  |  |  | √ |  |  |  |  |
| - Manually increase the target load as per boiler side instruction until 45 MW is reached. NOTE: Do NOT decrease load until 45 MW is reached as it may cause the CVs to fully close. MINIMUM load should be maintained at 30%L (45 MW). | TCE194_A1 |  |  |  |  | √ |  |  |  |  |
| - When the load increases more than 20 MW or HP bypass valve is fully closed, close the remaining starting drains (7drains). |  |  |  |  |  | √ |  |  |  |  |
| - After closing the drain valves, check that the green lamps go on. |  |  |  |  |  |  |  |  |  |  |
| - Close the cold reheat drain upstream non-return valve. (for verification again during start-up) |  |  |  |  |  |  |  |  |  |  |
| Note: - Steam pressure, temperature and load can be increased as fast as desired provided that: - Excessive turbine metal temperature differences are avoided. - Excessive differential expansion does not occur. - Regulate steam temperature and load to minimize metal temperature differentials as shown by the thermocouples. - If metal temperatures are high, it may be desirable to raise load and/or steam temperature rather quickly. If metal temperatures are low, it may be advisable to hold steam temperature as low as practical and increase load gradually. |  |  |  |  |  | √ |  |  |  |  |
| - WAIT for ACTUAL LOAD to reach 45 MW before selecting NORMAL OPERATION. Upon reaching 30% Load (45 MW), select NORMAL OPERATION > EXEC | TCA527_1 |  |  |  |  | √ |  |  |  |  |
| - Monitor thermal stress. Refer to appendices. After selecting NORMAL OPERATION, there is a Time Delay (TD) of 200 minutes before thermal stress limitation changes from its starting mode to normal/stop mode. Thermal Stress Condition for Different Start Up and Normal Condition | TURBINE CONTROL/ THERMAL STRESS |  |  |  |  | √ |  |  |  |  |
| - Set target load as per boiler instruction until 90 MW is reached. Note: >90MW we can set CCS | TCE194_A1 |  |  |  |  | √ |  |  |  |  |

## EXTRACTION STEAM SYSTEM START-UP

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Initial Condition for Servicing Extraction 5, 4, & 3 a. Pre start-up Checklist at extraction steam system completed |  |  |  |  | √ | √ | √ |  |  |  |
| b. Turbine Heat Soak on going on 3600rpm |  |  |  |  |  | √ |  |  |  |  |
| c. Deaerator Pre Warming Completed |  |  |  |  |  | √ |  |  |  |  |
| - Set LPH1 Cascade drains & alternate drain to auto - Set to auto Primary Drain of LPH1 | LCVHD11011 |  |  |  |  | √ |  |  |  |  |
| - Set to auto Secondary Drain of LPH1 | LCVHD11012 |  |  |  |  | √ |  |  |  |  |
| - Set LPH2 Cascade drains & alternate drain to auto - Set to auto Primary Drain of LPH2 | LCVHD11021 |  |  |  |  | √ |  |  |  |  |
| - Set to auto Secondary Drain of LPH2 | LCVHD11021 |  |  |  |  | √ |  |  |  |  |
| - Set LPH3 Cascade drains & alternate drain to auto - Set to auto Primary Drain of LPH3 | LCVHD11031 |  |  |  |  | √ |  |  |  |  |
| - Set to auto Secondary Drain of LPH3 | LCVHD11032 |  |  |  |  | √ |  |  |  |  |
| - Set HPH1 Cascade drains to auto - Set to auto Primary Drain of HPH1 | LCVHD11051 |  |  |  |  | √ |  |  |  |  |
| - Set to auto Secondary Drain of HPH1 | LCVHD11052 |  |  |  |  | √ |  |  |  |  |
| - Set HPH2 Cascade drains to auto - Set to auto Primary Drain of HPH2 | LCVHD11061 |  |  |  |  | √ |  |  |  |  |
| - Set to auto Secondary Drain of HPH2 | LCVHD11062 |  |  |  |  | √ |  |  |  |  |
| (Note: always observe for the vacuum pressure on the condenser) - Service extraction at LPH2 (extraction 5) - Gradually Open the Extraction 5 Drain before NRV and close after draining the condensate (about 3sec) | MVTS1395 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open the Extraction 5 Drain after NRV and close after draining the condensate (about 3sec) | MVTS1385 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open Extraction 5 MV then set to auto | MVTS1005 |  |  |  |  | √ |  |  |  |  |
| - Maintain temperature increase of 10°C/min on the heater | TICD11031 |  |  |  |  | √ |  |  |  |  |
| - Set to auto drained vales before and after NRV | MVTS1395 & MVTS1385 |  |  |  |  | √ |  |  |  |  |
| - Service extraction at LPH3 (extraction 4) - Gradually Open the Extraction 4 Drain before NRV and close after draining the condensate (about 3sec) | MVTS1394 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open the Extraction 4 Drain after NRV and close after draining the condensate (about 3sec) | MVTS1390 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open Extraction 4 MV then set to auto | MVTS1004 |  |  |  |  | √ |  |  |  |  |
| - Maintain temperature increase of 10°C/min on the heater | TICD11032 |  |  |  |  | √ |  |  |  |  |
| - Set to auto drained vales before and after NRV | MVTS1394 & MVTS1390 |  |  |  |  | √ |  |  |  |  |
| - Service extraction at Deaerator (extraction 3) - Gradually Open the Extraction 3 Drain before NRV and close after draining the condensate (about 3sec) | MVTS1393 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open the Extraction 3 Drain after NRV and close after draining the condensate (about 3sec) | MVTS1399 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open the Extraction 3 Drain after checked valve and close after draining the condensate (about 3sec) | MVTS1398 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open Extraction 3 MV then set to auto | MVTS1003 |  |  |  |  | √ |  |  |  |  |
| - Maintain temperature increase of 10°C/min on the deaerator | TICD1104 OR TIFW1010 |  |  |  |  | √ |  |  |  |  |
| - Set to auto drained vales before and after NRV and drain valve before check valve | MVTS1393, MVTS1398 & MVTS1399 |  |  |  |  | √ |  |  |  |  |
| - Servicing extraction 2 & 1, checked if Transfer region completed |  |  |  |  |  | √ |  |  |  |  |
| - Service extraction at HPH1 (extraction 2) - Gradually Open the Extraction 2 Drain before NRV and close after draining the condensate (about 3sec) | MVTS1392 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open the Extraction 2 Drain after NRV and close after draining the condensate (about 3sec) | MVTS1396 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open Extraction 2MV then set to auto | MVTS1002 |  |  |  |  | √ |  |  |  |  |
| - Maintain temperature increase of 10°C/min on the heater | TIFW1105 |  |  |  |  | √ |  |  |  |  |
| - Set to auto drained vales before and after NRV | MVTS1392 & MVTS1396 |  |  |  |  | √ |  |  |  |  |
| - Service extraction at HPH2 (extraction 1) - Gradually Open the Extraction 1 Drain before MV and close after draining the condensate (about 3sec) | MVTS1391 |  |  |  |  | √ |  |  |  |  |
| - Monitor the turbine bypass outlet press not to be affected | PIMS1021 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open the Extraction 1 Drain after MV and close after draining the condensate (about 3sec) | MVTS1397 |  |  |  |  | √ |  |  |  |  |
| - Gradually Open Extraction 1 MV then set to auto | MVTS1001 |  |  |  |  | √ |  |  |  |  |
| - Maintain temperature increase of 10°C/min on the heater | TIFW1106 |  |  |  |  | √ |  |  |  |  |
| - Set to auto drained vales before and after MV | MVTS1391 & MVTS1397 |  |  |  |  | √ |  |  |  |  |

## START LAST FIELD TRANSFORMER, RAPPER AND ASH HANDLING

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Initiate START at ESP panel | U-1205 U-1204 U-1203 U-1201 & 1202 |  |  |  |  |  | √ |  |  |  |
| - Monitor parameters - Current - Voltage - Spark per minute (SPM) |  |  |  |  |  |  | √ |  |  |  |
| - Ensure Rapping motor in AUTO - At DCS start Rapping motors |  |  |  |  |  | √ |  |  |  |  |
| - Ensure Ash handling in AUTO - Initiate SART ash handling system |  |  |  |  |  | √ |  |  |  |  |

## SOLID FIRING

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| a. ENSURE the following conditions are satisfied: - Solid Fuel Feeder READY. - Solid Fuel Feeder in REMOTE AUTO. - Solid Fuel Feeder Discharge Temperature NOT HIGH. - Solid Fuel Silo Level NOT LOW. - Solid Fuel Silo Manual Twin Knife Outlet Valve - Solid Fuel Feeder Outlet Isolation Valve (XV-CL1061A/B/C) OPEN. - Solid Fuel Feeder Speed Demand at MINIMUM. - Solid Fuel on Feeder Belt - Lower furnace differential pressure (dP) is at 650 mmH2O b. At 400°C - 450°C, INITIATE Solid Fuel Firing feeding the fuel by batch. Ten seconds (10s) burping and Sixty seconds (60s) rest interval for the next burping. Repeat interval of burping and rest until boiler temperature and pressure is in the proper range. c. Check CO, Sox and Lower Furnace Temperature rising reaction on each burping. Excess Oxygen will decrease as coal burn. NOTE: Wait for 5 minutes after coal feeding if the said coal batch did not burn. * Prioritize A and C side as the sides have burners for support in combustion. | XV-CL1061A/B/C |  |  |  | √ √ | √ √ | √ √ |  |  |  |
| b. Continuously RUN one feeder once verified that all indicators showing the Solid Fuel can burn properly, and the lower bed temperature average is > 600°C. START reducing Fuel Oil flow. Approximately: 2.55TPH coal =1TPH diesel | L – 1061 A, B, C |  |  |  |  | √ | √ |  |  |  |
| Once unit is stable, START another feeder and REDUCE fuel oil flow until minimum flow. | L – 1061 A, B, C |  |  |  |  | √ | √ |  |  |  |
| Once the unit is stable at a Lower Bed Permissible temperature of >650°C, ALLOW the third Solid Fuel Feeder to run at minimum feeder speed/feed rate. CONTINUE to reduce Fuel Oil flow until it equal the Solid Fuel heat input |  |  |  |  |  | √ |  |  |  |  |
| When Furnace temperature is > 700oC, START Retracting Start-up Burner. CONTINUE to remove Oil Burner until Lower Furnace temperature is > 750oC. When removing a burner from service, ALLOW the furnace temperature to recover and unit to stabilize. FOLLOW the start-up curve for increasing furnace temperature. |  |  |  |  |  | √ | √ |  |  |  |
| At full coal firing, START Limestone feeding System |  |  |  |  |  | √ | √ |  |  |  |
| ADJUST the Fuel Flow and Air Flow to maintain Furnace Temperature of 850oC~870oC. |  |  |  |  |  | √ | √ |  |  |  |
| Set Steam Temp. Controls and Combustion Controls on AUTO (BOILER AUTOMATIC CONTROL) when firing conditions are stable and the temperature and pressure control set points have been reached. At Boiler Load of >60% |  |  |  |  | √ | √ | √ |  |  |  |
| ADJUST the Feedwater supply to the boiler as necessary to maintain normal water level. Set to AUTO the Feedwater control as soon as possible and practicable after continuous Feedwater flow is established. |  |  |  |  |  | √ |  |  |  |  |
| Occasionally drain bed material from lower furnace to check if sintering is occurring at lower furnace. Check the size of bed material being drained. |  |  |  |  |  | √ | √ |  |  |  |

| Hours | T/H | T/H | T/H | T/H | T/H | MW |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Time | PAF | SAF | TAF | Oil Flow | Coal Flow | Load |  |  |  |
| 0 | 180 | 240 | 445 | 0 | 0 | 0 |  |  |  |
| 0.5 | 180 | 240 | 446 | 1 | 0 | 0 |  |  |  |
| 1 | 180 | 240 | 446 | 1.4 | 0 | 0 |  |  |  |
| 1.5 | 180 | 251 | 455 | 1.3 | 0 | 0 |  |  |  |
| 2 | 180 | 251 | 453 | 1.5 | 0 | 0 |  |  |  |
| 2.5 | 180 | 241 | 444 | 1.4 | 0 | 0 |  |  |  |
| 3 | 180 | 240 | 440 | 1.9 | 0 | 0 |  |  |  |
| 3.5 | 180 | 240 | 438 | 2.2 | 0 | 0 |  |  |  |
| 4 | 180 | 240 | 435 | 2.2 | 0 | 0 |  |  |  |
| 4.5 | 180 | 256 | 458 | 2.5 | 0 | 0 |  |  |  |
| 5 | 180 | 255 | 455 | 2.8 | 0 | 0 |  |  |  |
| 5.5 | 180 | 255 | 453 | 3 | 0 | 0 |  |  |  |
| 6 | 180 | 255 | 451 | 3 | 0 | 0 |  |  |  |
| 6.5 | 180 | 257 | 457 | 3.1 | 0 | 0 |  |  |  |
| 7 | 180 | 262 | 463 | 3.1 | 0 | 0 |  |  |  |
| 7.5 | 180 | 263 | 463 | 3.2 | 0 | 0 |  |  |  |
| 8 | 180 | 261 | 463 | 3.2 | 0 | 0 |  |  |  |
| 8.5 | 180 | 261 | 464 | 3.4 | 0 | 0 |  |  |  |
| 9 | 180 | 260 | 464 | 4.1 | 0 | 0 |  |  |  |
| 9.5 | 180 | 255 | 460 | 4 | 0 | 0 |  |  |  |
| 10 | 187 | 260 | 470 | 4.2 | 0 | 0 |  |  |  |
| 10.5 | 186 | 258 | 470 | 4.1 | 0 | 0 |  |  |  |
| 11 | 184 | 260 | 470 | 4.2 | 0 | 0 |  |  |  |
| 11.5 | 184 | 265 | 474 | 4.8 | 0 | 0 |  |  |  |
| 12 | 182 | 264 | 470 | 4.9 | 0 | 0 |  |  |  |
| 12.5 | 182 | 264 | 473 | 4.8 | 0 | 0 |  |  |  |
| 13 | 181 | 265 | 472 | 5 | 0 | 0 | STARTED BURPING |  |  |
| 13.5 | 180.5 | 265 | 472 | 5.4 | 0 | 0 |  |  |  |
| 14 | 180 | 264 | 468 | 5.9 | 0 | 0 |  |  |  |
| 14.5 | 190 | 260 | 474 | 6.2 | 0 | 0 |  |  |  |
| 15 | 200 | 240 | 466 | 6.5 | 2.1 | 0 |  |  |  |
| 15.5 | 200 | 236 | 461 | 6.2 | 2.4 | 0 |  |  |  |
| 16 | 182.5 | 232 | 441 | 6.8 | 0 | 0 | 1 CF CONTINUOUS. 1 BURP |  |  |

4.3.37 AT FULL COAL FIRING

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - Start limestone feeding system |  |  |  |  |  |  |  |  |  |  |
| - Start ALL ESP transformer |  |  |  |  |  |  |  |  |  |  |
| - Adjust PAF and SAF damper/air flow equal to RSV and put to REMOTE |  |  |  |  |  |  |  |  |  |  |
| - Put COAL MASTER to REMOTE and adjust boiler load using BOILER MASTER |  |  |  |  |  |  |  |  |  |  |
| - Service soot blowing system |  |  |  |  |  |  |  |  |  |  |

NOTE: At 230 T/H MSF, Approximately 75MW

- Put Staging to AUTO

- Put Boiler Master to Auto (Boiler Follow Mode) until 90 MW

GUIDELINES ON:

Eliminating the bed material intrude into windbox

Finding the most suitable staging air setting

| CONTROL POINT | CRITERIA | CONTROL RANGE |
| --- | --- | --- |
| Staging Air Dampers Control Mode | In any load | In Manual Disable the Auto mode for testing |
| PIFA 1088 (2nd air inlet pressure). Pressure corresponds to amount of bed material leading into windbox. | 130 MW above | Observe maximum pressure of 1300 - 1350 mmH20 Do not go beyond 1350 mmH20 - The pressure can be controlled through the adjustment of burner damper opening and staging dampers opening. - Gradually adjust staging dampers and observe for boiler reaction to find the most suitable settings. |
|  | 130 MW below | Observe maximum pressure of 1100 - 1250 mmH20 |
| DP1FG1084/1184 (Low furnace DP or Bed DP) | 130 MW above | Observe pressure of 1150-1250 mmH20 Most specially when PAF Bias is positive. Note: High PAF Bias - high erosion rate. |
|  | 130 MW below | Observe pressure not lower than 1100 mmH20 |

## BOTTOM ASH SCREW CONVEYOR

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| Make sure that the prestart checklist is properly done. Open cooling water shaft outlet gate valve (VCW1054,V-CW1058, V-CW1062, VCW1088) | VCW1054, V-CW1058, V-CW1062, VCW1088 |  |  |  |  | √ | √ |  |  |  |
| Open cooling water casing outlet gate valve (V-CW1052, V-CW1056, VCW1060, V-CW1084) | V-CW1052, V-CW1056, VCW1060, V-CW1084 |  |  |  |  |  | √ |  |  |  |
| Open cooling water shaft inlet globe valve (CW-1043, V-CW1046, VCW1049, V-CW1081) | CW-1043, V-CW1046, VCW1049, V-CW1081 |  |  |  |  |  | √ |  |  |  |
| Open cooling water shaft inlet globe valve (V-CW1044, V-CW1047, V-CW1050, V-CW1082) | V-CW1044, V-CW1047, V-CW1050, V-CW1082 |  |  |  |  |  | √ |  |  |  |
| Open cooling water inlet gate valve (V-CW1042, V-CW1045,VCW1048, V-CW1086) | V-CW1042, V-CW1045, VCW1048, V-CW1086 |  |  |  |  |  | √ |  |  |  |
| Select selector switch to remote on the local panel |  |  |  |  |  |  | √ |  |  |  |
| At DCS-OPS SELECT AND DISPLAY Bottom Ash Removal DCS graphics |  |  |  |  |  | √ |  |  |  |  |
| Select ash screw cooler (L- 1060A/B/C/D) through DCS and execute RUN command on the control template. | (L- 1060A/B/C/D |  |  |  |  | √ |  |  |  |  |
| Monitor all operating equipment for any abnormal noise, temperature and abnormal vibration. |  |  |  |  |  |  | √ |  |  |  |
| Open bottom ash screw cooler inlet isolation valve. (HVBH1060A/B/C/D) | HVBH1060A/B/C/D |  |  |  |  | √ |  |  |  |  |

## BOTTOM ASH SCREW COOLER in NORMAL OPERATION

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| Monitor the temperature and differential pressure of the bed material. |  |  |  |  |  | √ |  |  |  |  |
| Exercise every routine the pneumatic knife gate valve of bottom ash inlet chute going to the screw cooler. | HVBH 1060 A, B, C, D |  |  |  |  |  | √ |  |  |  |
| Monitor the cooling water inlet and return temperature and pressure. |  |  |  |  |  | √ | √ |  |  |  |
| Check for any abnormal noise and vibration in the ash screw cooler. Check that the motor and screw cooler runs smoothly. | L-1060 A, B, C, D |  |  |  |  |  | √ |  |  |  |
| Check for abrupt decrease in the speed of the screw cooler for this may indicate clogging within the screw cooler making the screw cooler turning hard. |  |  |  |  |  |  | √ |  |  |  |

## BOTTOM ASH COOLER SHUTDOWN OPERATION

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| Close bottom ash screw cooler inlet isolation valve. (HVBH1060A/B/C/D) | HVBH1060A/B/C/D |  |  |  |  | √ | √ |  |  |  |
| After some time, let the screw cooler run in order to drain the remaining bottom ash inside the cooler. Stop the bottom ash cooler through the DCS. Verify if the speed slows down. |  |  |  |  |  |  | √ |  |  |  |
| Check if the speed of the motor coasts down to zero (0) rpm. This indicated that the screw cooler shuts down successfully. |  |  |  |  |  |  | √ |  |  |  |
| Let the cooling water inlet and outlet valves open for 10 minutes’ after the screw cooler is stopped in order to cool down the ash screw cooler. |  |  |  |  |  | √ |  |  |  |  |

## BOTTOM ASH HANDLING START-UP FROM DCS (REMOTE)

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| SET the selector switch to “REMOTE POSITION” on the Local Operating Panel (LOP) | LOP |  |  |  |  |  | √ |  |  |  |
| At DCS-HMI OPEN Two-Way Valve (L-1094) into Silo. | L-1094 |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI Start Dust Collector Fan (S-1091) | S-1091 |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI Start Screw Conveyor (L-1092) | L-1092 |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI Start Bucket Elevator (L-1091) | L-1091 |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI Start Chain Conveyor (L-1090) | L-1090 |  |  |  |  | √ |  |  |  |  |
| MONITOR all operating equipment for any abnormal noise, temperature and abnormal vibration. |  |  |  |  |  |  | √ |  |  |  |

## BOTTOM ASH DISCHARGING OPERATION

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| CONNECT loading spout to the inlet of truck tank. PRESS the “UP” or “DOWN” button at the LOP-HP to adjust position of the loading spout. | LOP-HP |  |  |  |  |  | √ |  |  |  |
| Open Pneumatic KNIFE GATE VALVE (XV-1756) by PRESSING the “ON” button. Button Ash will discharge into truck tank through Pneumatic Knife Gate Valve and Loading spout. | XV-1756 |  |  |  |  |  | √ |  |  |  |
| CHECK automatic stop of ash discharging when level sensor(ZS-BH1754) detected High level on truck tank. “TANKER FULL” is indicated when truck tank is full. | ZS-BH1754 |  |  |  |  |  | √ |  |  |  |
| REMOVE Loading Spout from the truck tank inlet and return it to retracted position. |  |  |  |  |  |  | √ |  |  |  |
| MONITOR all operating equipment for any abnormal noise, temperature and abnormal vibration. |  |  |  |  |  |  | √ |  |  |  |

## BOTTOM ASH HANDLING SHUTDOWN FROM DCS (REMOTE)

| Equipment/Procedure | Tag no. |  | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| SET selector switch to REMOTE on the Local Operation Panel. | LOP |  |  |  |  |  |  | √ |  |  |  |
| At DCS-HMI Stop Chain Conveyor (L-1090) | L-1090 |  |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI Stop Bucket Elevator (L-1091) | L-1091 |  |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI Stop Screw Conveyor (L-1092) | L-1092 |  |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI Stop Dust Collector Fan (S-1091) | S-1091 |  |  |  |  |  | √ |  |  |  |  |
| At DCS-HMI CLOSE Two-Way Valve (L-1094) into Silo | L-1094 |  |  |  |  |  | √ |  |  |  |  |