SHutdown to bottle-up

| PR-ope-5004 |  |  |  |
| --- | --- | --- | --- |
| Prepared by: | R P. Del Mundo | Date Created: | 03-18-2024 |
| Reviewed by: | G T. Borja K R. Mendoza N L. Falcunit M P. Castro | Rev No. | 1 |
| Approved by: | Amatero Pete D. Ricablanca | Date Approved |  |

Document Revision Register Page

| Revision No. | Description | Date Created | Date Approved | Author |
| --- | --- | --- | --- | --- |
| 00 | Initial Issue | 07-01-2017 |  |  |
| 01 | Format Update | 03-18-2024 |  | Ralph P. Del Mundo |
|  | Change of company name and logo |  |  |  |
|  | Change of signatories |  |  |  |
| s |  |  |  |  |

| Equipment/Procedure | Tag no. | Operating Limits |  |  | Responsible |  |  |  |  | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Normal | Alarm | Trip | SS/SV | CRO | AO | WTP | MH |  |
| - CLOSE the following valves - MV-MS1391 - PCV-MS1001 (blow off valve) - HP bypass valve isolation valve - Auxiliary steam isolation valve |  |  |  |  |  | √ |  |  |  |  |
| - OPEN TG-Drain pots valve (upstream valve first then downstream) - DP-CR02 (V-CR1515 and V-CR1516) - DP-MS02 (V-MS1513 and V-MS1514) - DP-HR01 (V-HR1511 and V-HR1512) - DP-HR02 (V-HR1514 and V-HR1515) |  |  |  |  |  | √ |  |  |  |  |
| - OPEN HOT reheat blow off valve (MV-HR1391) to release hot reheat line pressure the CLOSE. |  |  |  |  |  | √ |  |  |  |  |
| - Fill the steam drum to +200mm |  |  |  |  |  | √ |  |  |  |  |
| - Fill the deaerator up to 0mm |  |  |  |  |  | √ |  |  |  |  |
| - CLOSE the BFP in service outlet valve (MV-FW1001/MV-FW1002) |  |  |  |  |  | √ |  |  |  |  |
| - STOP BFP in service |  |  |  |  |  | √ |  |  |  |  |
| - STOP in service chemical dosing pump |  |  |  |  |  |  |  |  |  |  |
| - CLOSE Deaerator Level control valve (LCV-CD1104) |  |  |  |  |  |  |  |  |  |  |
| - STOP in service make-up water pump |  |  |  |  |  |  |  |  |  |  |
| - Start reducing SUB (start-up burner) - Reduce Burner oil supply flow control (FIC-DO1043) to 25% - Press OFF button at DCS - Ensure Igniter will retract - Ensure oil gun will retract - Observe furnace pressure |  |  |  |  |  |  |  |  |  |  |
| - Set Diesel oil outlet pressure control (PCV-DO0002) and oil return line pressure control (PCV-DO1009) to MANUAL |  |  |  |  |  |  |  |  |  |  |
| - OPEN PCV-DO0002, PCV-DO1009 and FCV-DO1012 to 100% |  |  |  |  |  |  |  |  |  |  |
| - STOP in service diesel pump |  |  |  |  |  |  |  |  |  |  |
| - OPEN cold reheat header drain (V-CR1502 and V-CR1501) and Hot reheat header drain (V-HR1502 and V-HR1501) when pressure is almost 0kg/cm² (Upstream first the downstream valve when opening) |  |  |  |  |  |  |  |  |  |  |
| - Check RH and SH biasing damper opening should be 100% before shut off the draft balance system |  |  |  |  |  |  |  |  |  |  |
| - Adjust IDF set to 3 kg/cm² |  |  |  |  |  |  |  |  |  |  |
| - Set PAF and SAF inlet damper to MANUAL |  |  |  |  |  |  |  |  |  |  |
| - Reduce SAF inlet damper opening with 5% decrement while maintaining the furnace pressure at 15mmh2o up to 20%opening |  |  |  |  |  |  |  |  |  |  |
| - Reduce the PAF inlet damper opening with 1% decrement while maintaining furnace pressure around -15mmh2o up to 0% opening |  |  |  |  |  |  |  |  |  |  |
| - Initiate stop at PAF |  |  |  |  |  |  |  |  |  |  |
| - Initiate stop at FAB |  |  |  |  |  |  |  |  |  |  |
| - At <16% scoop tube position of H/C, HC will automatically se t to MANUAL CONTROL (maintain -15mmh2o of furnace pressure) |  |  |  |  |  |  |  |  |  |  |
| - Reduce SAF inlet damper opening with 5% decrement and ensure furnace pressure is maintain at -15mmh2o |  |  |  |  |  |  |  |  |  |  |
| - Initiate stop at SAF |  |  |  |  |  |  |  |  |  |  |
| - Reduce H/C position with 1% decrement while maintaining furnace pressure to -15mmh2o |  |  |  |  |  |  |  |  |  |  |
| - When H/C scoop tube reached to 0% position - Initiate stop at IDF - Change furnace pressure control to DAMPER CONTROL - OPEN DAMPER to 5% and ensure furnace pressure to -15mmh2o - Reduce damper opening around 2.5% until furnace pressure is reached around -20mmh2o to 20mmh2o |  |  |  |  |  |  |  |  |  |  |